#### CONTENTS

- INVITATION FOR BIDS (IFB)

- SECTION – 1 : INSTRUCTIONS TO BIDDERS (ITB)

- SECTION – 2 : FORM OF BID, QUALIFICATION INFORMATION AND LETTER OF ACCEPTANCE

- SECTION – 3 : GENERAL CONDITIONS OF CONTRACT

- SECTION – 4 : CONTRACT DATA

- SECTION – 5 : TECHNICAL SPECIFICATIONS

- SECTION – 6 : SCHEDULE OF QUANTITIES AND PRICES

- SECTION – 7 : BILL OF QUANTITIES

- SECTION – 8 : FORMS OF SECURITIES

- SECTION – 9 : DRAWINGS

7.	Submission of Bids:

Bids shall be in two parts

Part-I	:	Technical Bid	:	Containing full details of Technical Particulars, Commercial terms and conditions  and Bid Security.

Part-II	:	Price Bid	:	Containing schedule of quantities and prices.

Both these parts shall be furnished in separate sealed covers super scribing specification No., Bid Validity etc., with particulars as Part-I Technical Particulars and commercial terms and conditions and Part-II Price Bid. These sealed envelopes shall be placed in another sealed cover which shall be submitted before the due date and time specified.

a)	Part-I: Eligibility and Technical bid shall not contain any cost information whatsoever and this will be opened on the due date as mentioned in the table.

In case of bids where qualification requirements, technical suitability and other requirements are found to be inadequate, Part-II  “Price Bid” will be returned unopened.

b)	The date and time of opening of Part-II - Price Bid will be intimated to the qualified bidders after technical evaluation of all the bids is completed.

Not with standing anything stated above, SPDCL reserves the right to assess bidders capability to perform the contract should the circumstances warrant such assessment in overall interest of SPDCL. In this regard the decision of SPDCL is final.

CHIEF GENERAL MANAGER/ PROJECTS

APSPDCL :: TIRUPATI

SECTION 1

INSTRUCTIONS TO BIDDERS (ITB)

| ### SECTION 1 : INSTRUCTIONS TO BIDDERS |  |  |  |
| --- | --- | --- | --- |
| TABLES OF CLAUSES |  |  |  |
| A.GENERAL |  | D. SUBMISSION OF BIDS |  |
| 1. Scope of Bid 2. Source of Funds 3. Eligible Bidders 4. Qualification of the Bidder 5. One Bid per Bidder 6. Cost of Bidding 7. Site Visit B. BIDDING DOCUMENTS 8. Content of Bidding Documents 9. Clarification of Bidding Documents 10. Amendment of Bidding documents C. PREPARATION OF BIDS 11. Language of the Bid 12. Documents Comprising the Bid 13. Bid Prices 14. Currencies of Bid and Payment 15. Bid Validity 16. Bid Security 17. Alternative Proposals by Bidders 18. Format and Signing of Bid |  | 19. Sealing and Marking of Bids 20. Deadline for Submission of Bids 21. Late Bids 22. Modification and Withdrawal of Bids E. BID OPENING AND EVALUATION 23. Bid Opening 24. Process to be Confidential 25. Clarification of Bids 26. Examination of Bids and Determination of Responsiveness 27. Correction of Errors 28. Evaluation and Comparison of Bids F. AWARD OF CONTRACT 29. Award Criteria 30. Employer’s Right to Accept any Bid and to Reject any or all Bids. 31. Notification of Award & Signing of Agreement 32. Performance Security 33. Advance Payment and Security 34. Corrupt or Fraudulent Practices |  |

A. GENERAL

- SCOPE OF BID

  - The APSPDCL (referred to as Employer in these documents) invites bids for the construction of works (as defined in these documents and referred to as “the works”) detailed in the table given in IFB.  The bidders should submit bids for all of the works detailed in the table given in IFB.

  - The successful bidder will be expected to complete the works by the intended completion date specified in the Contract data.

- SOURCE OF FUNDS

Southern Power Distribution Company of A.P Limited., has taken funding from  Rural Electrification Corporation Limited., New Delhi for taking up the System Improvement works .

- ELIGIBLE BIDDERS

  - This Invitation for Bids is open to all bidders.  Any materials, equipment, and services to be used in the performance of the Contract shall have their origin in India.

  - All bidders shall provide in section 2, Forms of Bid and Qualification Information, a Statement that the bidder is not associated, nor has been associated in the past, directly or indirectly, with the Consultant or any other entity that has prepared the design, specifications, and other documents for the Project or being proposed as project Manager for the Contract.  A firm that has been engaged by the Borrower to provide consulting services for the preparation or supervision of the works, and any of its affiliates, shall not be eligible to bid.

  - Government-owned enterprises in the Employer’s country may only participate if they are legally and financially autonomous, operate under commercial law and are not a dependent agency of the Employer.

  - Bidders who are under a declaration of ineligibility for corrupt and fraudulent practices issued by APSPDCL in accordance with sub-clause 34.1 are not eligible.

- QUALIFICATION OF THE BIDDER

  - All bidders shall provide in Section 2, Forms of Bid and Qualification Information, a preliminary description of proposed work method and schedule, including drawings and charts, as necessary.

  - All bidders shall include the following information and documents with their bids in Section 2 compulsorily. Otherwise the bids will be evaluated based on the information available in the bid.

- Copies of original documents defining the constitution or legal status, place of registration, and principal place of business, written power of attorney of the signatory of the Bid to commit the Bidder.

- Total monetary value of construction work performed for each of the last five years.

- Experience in works of a similar nature and size for each of the last five years, and details of works under way or contractually committed; and clients who may be contacted for further information on those contracts;

- Major items of construction equipment proposed to carry out the Contract;

- Qualification and experience of key site management and technical personnel proposed for the Contract;

- Reports on the financial standing of the Bidder, such as profit and loss statements and auditor’s reports for the past five years;

- Evidence of adequacy of working capital for this contract (access to line(s) of credit and availability of other financial resources);

- Authority of seek references from the Bidder’s bankers;

- Information regarding any litigation, current or during the last five years, in which the Bidder is involved, the parties concerned, and disputed amount.

- Proposals for subcontracting components of the Works amounting to more than 10 percent of the Contract Price; and

- The proposed methodology of construction, backed with their construction equipment planning and deployment, duly supported with broad calculations and quality control procedures proposed to be adopted, justifying their capability of achieving the completion of work as per milestones specified within the stipulated period of completion.

4.3	BIDS FROM JOINT VENTURES ARE NOT ACCEPTABLE.

4.4 A.	To qualify for award of the contract, each bidder in his name should           have in the last five years  99-2000, 2000-2001, 2001-02, 2002-03, 2003-04.

- Achieved a minimum annual financial turnover (in all classes of Electrical Engineering construction works only) of 50% of Bid value during in any one year of the last five financial years and all other contracts awarded by SPDCL during 2004-05.

- Executed atleast one 33/11KV Sub-Station and 10KM of 33KV/11KV line satisfactorily.

- Shall have ‘A’ Grade Electrical Contractor’s license from Government of Andhra Pradesh.

B.	Each bidder should further demonstrate:

- Availability (either owned or leased or by procurement of the key and critical equipment for this work.

Note:

- Availability for this work of a Project Manager with not less than five years’ experience in construction of similar Electrical Engineering works and other key personnel with adequate experience as required, and this person shall be incharge of works if contract is awarded.

- Liquid assets and credit facilities of not less than Rs.50.0 lakhs (Credit lines/ letter of credit from Banks, etc)

  - To qualify for a package of contracts made up of this and other contracts for which bids are invited in the IFB, the bidder must demonstrate having resources sufficient to meet the aggregate of the qualifying criteria for the individual contracts.

  - Sub-contractor’s experience and resources shall not be taken into account in determining the bidder’s compliance with the qualifying criteria.

  - Even though the bidders meet the above qualifying criteria, they are subject to be disqualified if they have:

- made misleading or false representations in the forms, statements and attachments submitted in proof of the qualification requirements; and/or

- record of poor performance such as abandoning the works, not properly completing the contract, inordinate delays in completions, litigation history, or financial failures etc.

  - The bidders have to furnish an undertaking in the prescribed format given in

Section-2 disclosing their relationship with the officers/Directors of APTRANSCO/DISCOM failing which the tenders will be rejected. Any false information furnished in the declaration will render the contract liable for termination as well as recovery of damages.

5.  ONE BID PER BIDDER

5.1	DELETED

6.  COST OF BIDDING

6.1	The bidder shall bear all costs associated with the preparation and submission of his Bid, and the Employer will in no case be responsible and liable for those costs.

7.  SITE VISIT

7.1	The Bidder, at the Bidder’s own responsibility and risk is required to visit & examine the Site of Works and its surroundings and obtain all information that may be necessary for preparing the Bid and entering into a contract for construction of the Works.  The costs of visiting the Site shall be at the Bidder’s own expense.

B.BIDDING DOCUMENTS

8.  CONTENT OF BIDDING DOCUMENTS

8.1	The set of bidding documents comprises the documents listed in the table below and addenda issued in accordance with Clause 10 :

Section	Invitation for Bids

- Instruction to Bidders

- Forms of Bid and Qualification Information

- Conditions of Contract

- Contract Data

- Specifications

- Schedule of quantities and prices

- Bill of quantities

- Forms of Securities

- Drawings

8.2	One set of copy schedule as original and other set (xerox copy) as copy should be completed and submitted with the bid.

9.  CLARIFICATION OF BIDDING DOCUMENTS

9.1	A prospective bidder requiring any clarification of the bidding documents may notify the Employer in writing or by cable (hereinafter “cable” includes telex and Facsimile) at the Employer’s address indicated in the invitation to bid.  The Employer will respond to any request for clarification, which he received earlier than 15 days prior to the deadline for submission of bids.  Copies of the Employer’s response will be forwarded to all purchasers of the bidding documents, including a description of the enquiry but without identifying its source.

10.AMENDMENT OF BIDDING DOCUMENTS

10.1	Before the deadline for submission of bids, the Employer may modify the bidding documents by issuing addenda.

  - Any addendum thus issued shall be part of the bidding documents and shall be communicated in writing or by cable to all the purchasers of the bidding documents.  Prospective bidders shall acknowledge receipt of each addendum by cable to the Employer.

10.3	to give prospective bidders reasonable time in which to take an addendum into account in preparing their bids, the Employer shall extend as necessary the deadline for submission of bids, in accordance with Sub - Clause 20.2 below.

C. PREPARATION OF BIDS

11.  LANGUAGE OF THE BID

11.1	All documents relating to the bid shall be in the English language

12.  DOCUMENTS COMPRISING THE BID

  - The bid submitted by the bidder shall comprise the following in two parts as part I Technical Bid and PartII Price bid in two separate sealed covers superscribing Specification No. Bid security details, validity etc. and these two parts shall be placed in another sealed cover.

- Part-I  Bid Security as per clause 16 of ITB(Section-1)

- Part-I  Technical Bid information (in the format indicated in Section 2)

- Part-II Price Bid as per section-6

And any other materials required to be completed and submitted by bidders in accordance with these instructions.  The documents listed under Sections 2, 4 and 7 mentioned in Sub-Clause 8.1 of section-I shall be filled in without exception.

- BID PRICES

  - The contract shall be for the whole works as described in Sub-Clause 1.1, based on the priced Bill of Quantities submitted by the Bidder.

  - The bidder shall fill in rates and prices for all items of the Works described in the Bill of quantities. Items for which no rate or price is entered by the bidder will not be paid for by the Employer when executed and shall be deemed covered by the other rates and prices in the Bill of Quantities, Corrections, if any, shall be made by crossing out, initialing, dating and rewriting.

  - All duties, taxes, and other levies payable by the contractor under the contract, or for any other cause shall be included in the rates, prices and total Bid Price submitted by the Bidder.

  - The rates and prices quoted by the bidder shall be fixed throughout the contract period.

14.  CURRENCIES OF BID AND PAYMENT

  - The unit rates and the prices shall be quoted by the bidder entirely in Indian Rupees.

15.  BID VALIDITY

  - Bids shall remain valid for a period not less than Ninety days after the deadline date of bid submission specified in Clause 20.  A bid valid for a shorter period shall be rejected by the Employer as non-responsive.

  - In exceptional circumstances, prior to expiry of the original time limit, the Employer may request that the bidders may extend the period of validity for a specified additional period.  The request and the bidder’s responses shall be made in writing or by cable.  A bidder may refuse the request without forfeiting his bid security.  A bidder agreeing to the request will not be required or permitted to modify his bid except as provided in 15.3 hereinafter, but will be required to extend the validity of his bid security for a period of the extension, and in compliance with Clause 16 in all respects.

  - In the case of contracts in which the Contract Price  is fixed (not subject to price variation), in the event that the Employer requests and the Bidder agrees to an extension of the validity period, the contract price, if the Bidder is selected for award shall be the bid price corrected as follows:

  - Bid evaluation will be based on the bid prices without taking into consideration the above correction.

16.  BID SECURITY

    - The Bidder shall furnish, as part of his Bid, a Bid security compulsorily in the amount as shown in column 4 of the table of IFB for this particular work. This bid security shall be in favor of Accounts Officer/CPR / APSPDCL / payable at Tirupati and may be in one of the following forms:

-  a bank guarantee issued by a nationalized / scheduled bank located in India acceptable to the Employer in the form given in Section 8: Annexure-A.

- Bank draft in favour of Accounts Officer/CPR / APSPDCL / TIRUPATI, payable Tirupati drawn on any scheduled Bank.

- The existing PEMD holders whose PEMD is valid for 135 days are eligible to quote for one lot only.

- Any security other than the type of Bid security mentioned above will not be accepted.

16.2	Bank guarantees (and other instruments having fixed validity) issued as surety for the bid shall be valid upto 135 days from the date of bid opening.

16.3    Any bid not accompanied by an acceptable Bid Security and not secured as

indicated in Sub-Clauses 16.1 and 16.2 above shall be rejected by the 	Employer as non-responsive.

  - The Bid Security of the unsuccessful bidder will be returned within 28 days of the end of the bid validity period specified in Sub-Clause 15.1.

16.5	The Bid Security of the successful bidder will be discharged when the bidder has signed the Agreement and furnished the required performance Security.

16.6	The Bid Security may be forfeited

- if the Bidder withdraws the Bid after Bid opening during the period of Bid validity:

- if the Bidder does not accept the correction of the Bid Price, pursuant to Caluse 27; or

- in the case of a successful Bidder, if the Bidder fails within the specified time limit to

- sign the Agreement or

- furnish the required performance Security.

17.   ALTERNATIVE PROPOSALS BY BIDDERS

17.1	Bidders shall submit offers that comply with the requirements of the bidding documents, including the basic technical design as indicated in the drawing and specifications.  Alternatives will not be considered.

18.	FORMAT AND SIGNING OF BID

18.1	The Bidder shall prepare one original and one copy of the documents comprising the bid as described in Clause 12 of these Instruction s to Bidders bound with the volume containing the Forms of Bid, and clearly marked “ORIGINAL” and “COPY” as appropriate.  In the event of discrepancy between them, the original shall prevail.

  - The original and copy of the Bid shall be typed or written in indelible ink and shall be signed by a person or person duly authorized to sign on behalf of the Bidder, pursuant to Sub-Clauses 4.4.  All pages of the bid where entries or amendments have been made shall be initialed by the person or persons signing the bid.

  - The Bid shall contain no alterations or additions, except those to comply with instructions, issued by the Employer, or as necessary to correct errors made by the bidder, in which case such corrections shall be initialed by the person or persons signing the bid and all officers present and other company representatives also.

  - The Bidder shall furnish information as described in the form of Bid on commissions or gratuities, if any, paid or to be paid to agents relating to this Bid, and to contract execution if the Bidder is awarded the contract.

##### D. SUBMISSION OF BIDS

- SEALING AND MARKING OF BIDS

  - The Bidder shall seal the original and copy of the Bid in separate envelopes, duly marking the envelopes as “ORIGINAL” and “COPY”.  These envelopes (called as inner envelopes) shall then be put inside one outer envelope.

  - The inner and outer envelopes shall

- be addressed to the Employer at the following address:

Chief General Manager/Projects,

O/o. C.M.D. APSPDCL,

D.No.19-3-13 (M), Upstairs,

Tirupati -517501

- bear the following identification:

- Bid for System Improvement Project work in

- Bid Reference No.SKL 01-2001 (insert number)

- Do not open before          (time and date for bid opening, as per Clause 20)

  - In addition to the identification required in Sub-Clause 19.2, the inner envelopes shall indicate the name and address of the bidder to enable the bid to be returned unopened incase it is declared late, pursuant to Clause 21

19.4	If the outer envelope is not sealed and marked as above, the Employer will assume no responsibility for the misplacement or premature opening of the bid.

20.	DEADLINE FOR SUBMISSION OF THE BIDS

20.1	Bids must be received by the Employer at the address specified above not later than 12.00 hours on 01.07.2004.

In the event of the specified date for the submission of bids declared a holiday for the Employer, the Bids will be received up-to the appointed time on the next working day.

20.2	The Employer may extend the deadline for submission of bids by issuing an amendment in accordance with Clause 10, in which case all rights and obligations of the Employer and the bidders previously subject to the original deadline will then be subject to the new deadline.

21.	LATE BIDS

21.1	Any Bid received by the Employer after the deadline prescribed in Clause 20 will be returned unopened to the bidder.

22.  MODIFICATION AND WITHDRAWAL OF BIDS

22.1	Bidders may modify or withdraw their bids by giving notice in writing before the deadline prescribed in Clause 20.

22.2	Each Bidder’s modification or withdrawal notice shall be prepared, sealed, marked, and delivered in accordance with clause 18 & 19, with the outer and inner envelopes additionally marked “MODIFICATION” or “WITHDRAWAL” as appropriate.

22.3	No bid may be modified after the deadline for submission of Bids.

22.4	Withdrawal or modification of a Bid between the deadline for submission of bids and the expiration of the original period of bid validity specified in Clause 15.1 above or as extended pursuant to Clause 15.2 may result in the forfeiture of the Bid security pursuant to Clause 16.

22.5	Bidders may only offer discounts to, or otherwise modify the prices of their Bids by submitting Bid modifications in accordance with this clause, or included in the original Bid submission.

### E. BID OPENING AND EVALUATION

23.  BID OPENING

23.1	The Employer will open all the Bids received (except those received late), including modification made pursuant to Clause 22, in the presence of the Bidders or their representatives who choose to attend at the time on the date and the place specified.  In the event of the specified date of Bid opening being declared a holiday for the Employer, the Bids will be opened at the appointed time and location on the next working day.

23.2	Envelopes marked “WITHDRAWAL” shall be opened and read out first, Bids for which an acceptable notice of withdrawal has been submitted pursuant to Clause 22 shall not be opened.

23.3	The Bidder’s names, the Bid prices, the total amount of each Bid and of any alternative Bid (if alternatives have been requested or permitted), any discounts, Bid modification and withdrawals, the presence or absence of Bid security, and such other details as the Employer may consider appropriate, will be announced by the Employer at the opening, Any Bid price, discount, or alternative Bid price which is not read out and recorded at Bid opening will not be taken into account in Bid evaluation.

23.4	The Employer shall prepare minutes of the Bid opening, including the information disclosed to those present in accordance with Sub-Clause 23.3.

24.  PROCESS TO BE CONFIDENTIAL

24.1	Information relating to the examination, clarification, evaluation, and comparison of Bids and recommendations for the award of a contract shall not be disclosed to Bidders or any other persons not officially concerned with such process until the award to the successful Bidder has been announced.  Any effort by a Bidder to influence the Employer’s processing of Bids or award decisions may result in the rejection of his Bid.

25.  CLARIFICATION OF BIDS

25.1	To assist in the examination, evaluation, and comparison of Bids, the Employer may, at his discretion, ask any Bidder for clarification of his Bid, including breakdowns of unit rates.  The request for clarification and the response shall be in writing or by cable, but no change in the price or substance of the Bid shall be sought, offered, or permitted except as required to confirm the correction of arithmetic errors discovered by the Employer in the evaluation of the Bids in accordance with Clause 27.

25.2	Subject to sub-Clause 25.1, no Bidder shall contact the Employer on any matter relating to its bid from the time of the bidding opening to the time the contract is awarded.  If the Bidder wishes to bring additional information to the notice of the Employer, he should do so in writing.

25.3	Any effort by the Bidder to influence the Employer in the Employer’s bid evaluation, bid comparison or contract award decisions may result in the rejection of the Bidder’s bid.

26.  EXAMINATION OF BIDS AND DETERMINATION OF RESPONSIVENESS

26.1	Prior to the detailed evaluation of Bids, the Employer will determine whether each Bid (a) meets the eligibility criteria defined in Clause 3; (b) has been properly signed; (c) is accompanied by the required securities and ; (d) is substantially responsive to the requirements of the Bidding documents.

26.2	A substantially responsive Bid is one which conforms to all the terms, conditions, and specifications of the Bidding documents, without material deviation or reservation.  A material deviation or reservation is one (a) which affects in any substantial way the scope, quality, or performance of the 
Works; (b) which limits in any substantial way, inconsistent with the Bidding documents, the Employer’s rights or the Bidder’s obligations under the Contract, or (c) whose rectification would affects unfairly the competitive position of other Bidders presenting substantially responsive Bids.

26.3	If a Bid is not substantially responsive, it will be rejected by the Employer, and may not subsequently be made responsive by correction or withdrawal of the non-confirming deviation or reservation.

27.  CORRECTION OF ERRORS

27.1	Bids determined to be substantially responsive will be checked by the Employer for any arithmetic errors.  Errors will be corrected by the Employer as follows:

- Where there is a discrepancy between the rates in figures and in words, the rate in words will govern, and

- Where there is a discrepancy between the unit rate and the line item total resulting from multiplying the unit rate by the quantity the unit rate as quoted will govern.

  - The amount stated in the Bid will be adjusted by the Employer in accordance with the above procedure for the correction of errors and with the concurrence of the Bidder, shall be considered as binding upon the Bidder.  If the Bidder does not accept the corrected amount the Bid will be rejected, and the Bid security may be forfeited in accordance with Sub-Clause 16.6 (b).

28.  EVALUATION AND COMPARISION OF BIDS

  - The Employer will evaluate and compare only the Bids determined to be substantially responsive in accordance with Clause 26.

  - In evaluating the Bids, the Employer will determine for each Bid the evaluated Bid price by adjusting the Bids price as follows:

- making any correction for errors pursuant to Clause 27; or

- making an appropriate adjustments for any other acceptable variations, deviations and

- making appropriate adjustments to reflect discounts or other price modifications offered in accordance with Sub Clause 22.5

  - The Employer reserves the right to accept or reject any variation, deviation, or alternative offer.  Variations, deviations, and alternative offers and other factors, which are in excess of the requirements of the Bidding documents or otherwise result in unsolicited benefits for the Employer shall not be taken into account in Bid evaluation.

  - The estimated effect of the price adjustment conditions under Clause 47 of the Conditions of Contract, during the period of implementation of the Contract, will not be taken into account in Bid evaluation.

  - If the Bid of the successful Bidder is seriously unbalanced in relation to the Engineer’s estimate of the cost of work to be performed under the contract, the Employer may require the Bidder to produce detailed price analyses for any or all items of the Bill of Quantities, to demonstrate the internal consistency of those prices with the construction methods and schedule proposed.  After evaluation of the price analyses, the Employer may require that the amount of the performance security set forth in Clause 32.1 increased at the expense of the successful Bidder to a level sufficient to protect the Employer against financial loss in the event of default of the successful Bidder under the Contract.

### F. AWARD OF CONTRACT

29.  AWARD CRITERIA

29.1	Subject to Clause 32, the Employer will award the Contract to the Bidder whose Bid has been determined to be substantially responsive to the Bidding documents and who has offered the lowest evaluated Bid Price, provided that such Bidder has been determined to be (a)eligible in accordance with the provisions of Clause 3, (b)qualified in accordance with the provisions of clause 4.

30	EMPLOYER’S RIGHT TO ACCEPT ANY BID AND TO REJECT ANY OR ALL BIDS

  - Notwithstanding Clause 29, the Employer reserves the right to accept or reject any Bid, and to cancel the Bidding process and reject all Bids, at any time prior to the award of Contract, without thereby incurring any liability to the affected Bidder or Bidders or any obligation to inform the affected Bidder or Bidders of the grounds for the Employer’s action.

  - The Employer reserves the right to award not more than One Lot in case     the bidder is successful in more than one bid or Lot.

- NOTIFICATION OF AWARD AND SIGNING OF AGREEMENT

  - The Bidder whose Bid has been accepted will be notified of the award by the Employer prior to expiration of the Bid period by cable, telex or facsimile confirmed by registered letter. This letter (hereinafter in the Conditions of Contract called the “Letter of Acceptance”) will state the sum that the Employer will pay the Contractor in consideration of the execution, completion, and maintenance of the works by the contractor as prescribed by the Contract (hereinafter and in the Contract called the ”Contract Price”).

  - The notification of award will constitute the formation of the Contract, subject only to the furnishing of a performance security in accordance with the provisions of Clause 32 and signing of agreement.

  - The Agreement will incorporate all agreements between the Employer and the successful Bidder.  It will be signed by the Employer and sent to the successful Bidder, within 28 days following the notification of award along with the Letter of Acceptance.  Within 21 days of receipt, the successful Bidder will sign the Agreement and deliver it to the Employer.

  - Upon the furnishing by the successful Bidder of the performance Security, the Employer will promptly notify the other Bidders that their Bids have been unsuccessful.

- PERFORMANCE SECURITY

  - Within 21 days of receipt of the Letter of Acceptance, the Successful Bidder shall deliver to the Employer a Performance Security in any of the forms given below for an amount equivalent to 5% of the Contract price plus additional security for unbalanced Bids in accordance with Clause 29.5:

- a bank guarantee in the form given in Section 8; or

- Bank draft, in favour of Accounts Officer/CPR/APSPDCL/Tirupati, payable at Tirupati drawn on any scheduled Bank.

  - If the performance security is provided by the successful Bidder in the form of a Bank Guarantee, it shall be issued either (a) at the Bidder’s option, by a            Nationalized/Scheduled Indian Bank or (b) by a foreign Bank located in India and acceptable to the Employer.

  - Failure of the successful Bidder to comply with the requirements of Sub-Clause 32.1 shall constitute sufficient grounds for cancellation of the award and forfeiture of the Bids Security.

33.  ADVANCE PAYMENT AND SECURITY:

### DELETED

34.  CORRUPT OR FRAUDULENT PRACTICES.

34.1	APSPDCL Bidders/ Contractors/ Contractors observe the highest standard of ethics during the procurement and execution of such contracts.  In pursuance of this policy, APSPDCL:

- Defines, for the purposes of this provision, the terms set forth below as follows:

- “Corrupt Practice” means the offering, giving, receiving or soliciting of any thing of value to influence the action of a public official in the procurement process or in contract execution, and

- “Fraudulent Practice” means a misrepresentation of facts in order to influence a procurement process or the execution of a contract to the detriment of the Borrower, and includes collusive practice among Bidders (prior to or after bid submission) designed to establish bid prices at artificial non-competitive levels and to deprive the Borrower of the benefits of free and open competition.

- Will reject a proposal for award if it determines that the Bidder recommended for award has engaged in corrupt or fraudulent practices in competing for the contract in question.

- Will declare a firm ineligible, either indefinitely or for a stated period of time, to be awarded a Bank financed contract if it at any time determines that the firm has engaged in corrupt or fraudulent practices in competing for, or in executing a Bank-financed contract.

34.2	Furthermore, Bidders shall be aware of the provision stated in sub-clause 23.2 and sub-clause 59 of the General Conditions of Contract.

SECTION 2

FORM OF BID, QUALIFICATION INFORMATION

AND LETTER OF ACCEPTANCE

TABLE OF FORMS:

- CONTRACTOR’S BID

- QUALIFICATION INFORMATION

- LETTER OF ACCEPTANCE

- NOTICE TO PROCEED WITH THE WORK

- AGREEMENT FORM

- DECLARATION FORM

CONTRACTOR’S BID

Description of the Works:______________________________________________________________________________________________________________________________________________________________________________________________

BID

To	:  Chief General Manager /Projects, Southern Power Distribution Company of A.P. Limited, D.No. 19-3-13 (M), Renigunta Road, Tirupati-517501

(the Employer).

Gentlemen,

We offer to execute the Works described above in accordance with the Conditions of Contract accompanying this Bid for the Contract Price of ____________ (in figures) (________________________________________________) in letters.

The advance payments required is : Rupees_________________

This Bid and your written acceptance of it shall constitute a binding contract between us.  We understand that you are not bound to accept the lowest or any Bid you receive.

Commission or gratuities, if any, paid or to be paid by us to agents relating to this Bid, and to contract execution if we are awarded the contract, are listed below:

Name and address of agent		Amount	Purpose of Commission on gratuity/

……………………………….		…………..	………………………………………..

……………………………….		…………..	………………………………………..

……………………………….		…………..	………………………………………..

(if none, state “none”)

_____________________________

We hereby confirm that this Bid complies with the Bid Validity and Bid Security required by the Bidding documents.

We attach herewith our current income-tax clearance certificate.

Yours faithfully,

Authorized Signature:

Name & Title of Signatory : _______________________________________________

Name of Bidder : _________________________________________________

Address : __________________________________________________

2. To be filled by Bidder, together with his particulars and date of submission at the bottom of the form of Bid.

QUALIFICATION INFORMATION

The information to be filled in by the Bidder in the following pages will be used for purposes of post - qualification as provided for in Clause 4 of the instructions to Bidders.  This information will not be incorporated in the Contract.

- For Individual Bidders

  - Constitution or legal status of Bidder

(Attach Copy)

Place of Registration:

Principal place of business:

Power of Attorney of Signatory of Bid

(Attach)

  - Total value of Electrical Engineering Construction

  - Work performed in the last five years.  			1999 - 2000

(in Rs. Lakhs)							2000 -	2001

2001 - 2002

2002 -2003

2003 - 2004

    - Work performed as prime contractor (in the same name) on works of a similar nature over the last five years.

| Project Name | Name of Employer | Description of work | Contract No. | Value of contract (Rs. Lakhs) | Date of issue of work order | Stipulated period of completion | Actual date of com- Pletion | Remarks Explaining reasons for delay and work completed |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Note: 	The certificates shall be attested by the Divisional Engineer, Construction in

Charge of the work.

13.2	Quantities of work executed as prime contractor (in the same name and style) in the last five years:” 1999 – 2000, 2000 – 01, 2001-02,2002-2003, 2003-04.

Year		Name of the work Qty in KM			Amount in Rs. Lakhs

I) Erection of 33/11 KV lines

2) Names of 33/11KV Sub-stations.

- Enclose certificate(s) from the Engineer(s) in-charge.

@  The item of work for which data is requested should tally with that specified in ITB clause 4.5 C.

**   Immediately preceding the financial year in which bids are received.

  - Information on Bid Capacity (works for which bids have been submitted and works which are yet to be completed) as on the date of this bid.

- Existing commitments and on-going works in APSPDCL and other works.

| Description of work | Place & State | Contract No. & Date | Name and Address of employer | Value of Contract (Rs. Lakhs) | Stipulated period of completion (RS. Lakhs) | Value of works remaining to be | Anticipated date of completion |
| --- | --- | --- | --- | --- | --- | --- | --- |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) |

- Works for which bids already submitted:

| Description Of Work | Place & State | Estimated value of works (Rs. Lakhs) | Stipulated period of | Date when decision is completion | Remarks if any expected |
| --- | --- | --- | --- | --- | --- |
| (1) | (2) | (3) | (4) | (5) | (6) |

- Enclose certificate  (s) from the Engineer (s)-in-Charge.

  - The following items of Contractor’s Equipment are essential for carrying out the Works.  The Bidder should list all the information requested below.  Refer also to Sub Clause 4.2 (d) of the Instructions of Bidders.

| Item of equipment | Requirement No. Capacity | Availability proposals Owned/leased/ to be procured | Nos./ capacity | Age/ condition | Remarks (from whom to be purchased) |
| --- | --- | --- | --- | --- | --- |

  - Qualifications and experience of key personnel proposed for administration and execution of the Contract, Attach biographical data.  Refer also to Sub Clause 4.2 (e) of instructions to Bidders and Sub Clause 9.1 of the Conditions of Contract.

| Position Project Manager Etc. | Name | Qualification | Years of experience (general) | Years of experience in the proposed position |
| --- | --- | --- | --- | --- |

  - Proposed subcontracts and firms involved (Refer ITB Clause 4.2 (I)

| Section Of the works | Value of Sub-Contract | Sub-Contractor (name and address) | Experience in Similar work |
| --- | --- | --- | --- |

  - Financial reports for the last five years: balance sheets, profit and loss statements, auditors reports (in case of companies/corporation) etc.  List them below and attach copies.

  - Evidence of access to financial resources to meet the qualification requirements: cash in hand, lines of credit, etc.  List them below and attach copies of support documents.

1.10	Name, address and telephone, telex, and fax numbers of the Bidders’ bankers who may provide references if contacted by the Employer.

  - Information on litigation history in which the Bidder is involved.

| Other party (ies) | Employer | Cause of dispute | Amount involved | Remarks showing present status |
| --- | --- | --- | --- | --- |

  - Statement of compliance under the requirements of Sub Clause 3.2 of the instructions to Bidders.

  - Proposed work method and schedule.  The Bidder should attach descriptions, drawings and charts as necessary to comply with the requirements of the Bidding documents.  (Refer ITB Clause 4.1 and 4.2 (k)).

- Additional Requirements

2.1	Bidders should provide any additional information required to fulfill the requirements of Clause 4 of the instructions to the Bidders, if applicable.

LETTER OF ACCEPTANCE

(Letterhead paper of the Employer)

____________________(date)

To:__________________________________________________________(name and

address of the Contractor).

Dear Sirs,

This is to notify you that your Bid dated_________for execution of the_________

_______________________________________________________________

(name

of the contract and identification number, as given in the instructions to Bidders)1 for the  Contract Price of Rupees__________________________________________________

____________________________________(___________) (Amount in words and

Figures), as corrected and modified in accordance with the instructions to Bidders’ is hereby accepted by our Agency.

You are hereby requested to furnish Performance Security, plus additional security for unbalanced bids in terms of ITB clause 28.2 in the form detailed in Para 32.1 or ITB for an amount of Rs.__________ within 21 days of the receipt of this letter of acceptance valid up-to 28 days from the date of expiry of Defects Liability Period i.e.

Up-to ………… and sign the contract, failing which action as stated in Para 32.3 of ITB will be taken.

Yours faithfully,

Authorized Signature

Name and Title of Signatory

Name of Agency

Chief General Manager/ Projects,

Southern Power Distribution Company of A.P. Limited

D.No.19-3-13 (M)

Renigunta Road

Tirupati - 517501

1.	Delete ”correct and” or “and modified” if only one of these actions applies.  Delete “as corrected and modified in accordance with the Instructions to Bidders” if corrections or modifications have been effected.

2.	To be used only if the Contractor disagrees in his Bid with the Technical Expert proposed by the Employer in the ”Instructions to Bidders.”

ISSUE OF NOTICE TO PROCEED WITH THE WORK

(Letterhead of the Employer)

____________(date)

To

_____________________(Name and Address of the Contractor)

_____________________

_____________________

Dear Sirs,

Pursuant to your furnishing the requisite security as stipulated in ITB clause 32.1 and signing of the contract for the construction of -------------------------@ a Bid price of Rs.------------------------, you are hereby instructed to proceed with the execution of the said works in accordance with the contract documents.

Yours faithfully,

Chief General Manager/

Projects,

Southern Power Distribution Company of A.P. Limited

D.No.19-3-13 (M)

Renigunta Road

Tirupati - 517501

(Signature, name and title of signatory

Authorized to sign on behalf of Employer)

AGREEMENT FORM

Agreement

This agreement, made the -------------------------day of --------------- Year --------between

---------------------------------------------------------------------------------------------------------------

--------------------------------------------------(Name and Address of Employer).

(Hereinafter called “the Employer)” and------------------------------------------------------------

---------------------------------------------------------------------------------------------------------------

-----------------------------------------------[Name and Address of Contractor] (hereinafter called “the Contractor” of the other part).

Whereas the Employer is desirous that the Contractor execute----------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------)

Name and identification number of Contract] (hereinafter called “the Works’) and the Employer has accepted the Bid by the Contractor for the execution and completion of such Works and the remedying of any defects therein, at a cost of Rs………………….

NOW THIS AGREEMENT WITNESS as follows:

1.	In this Agreement, words and expression shall have the same meanings as are respectively assigned to them in the Conditions of contract hereinafter referred to, and they shall be deemed to form and be read and construed as part of this Agreement.

2.	In consideration of the payments to be made by the Employer to the Contractor as hereinafter mentioned, the Contractor hereby covenants with the Employer to execute and complete the Works and remedy and defects therein conformity in all aspects with the provisions of the Contracts.

3.	The Employer hereby covenants to pay the Contractor in consideration of the execution and completion of the Works and the remedying the defects wherein the Contract price or such other sums as may become payable under the provisions of the Contract at the times and in the manner prescribed by the Contract.

4.	The following documents shall be deemed to form and be read and construed as part of this Agreement, viz.:

i)	Letter of Acceptance;

ii)	Notice to proceed with the works;

iii)	Contractor’s Bid;

iv)	Contract Data;

v)	Conditions of Contract;

vi)	Specifications;

vii)	Drawings;

viii)	Bill of Quantities; and

ix)	Any other document listed in the Contract Data as forming part of the Contract.

In witness where of the parties there to have caused this Agreement to be executed the day and years first before written.

The Common Seal of --------------------------------------------------------

Was hereunto affixed in the presence of:

Signed, Sealed and delivered by the said---------------------------------------------------------

---------------------------------------------------------------------------------------------------------------

---------------------------------------------------------------------------------------------------------------

in the presence of:

Binding Signature of Employer	---------------------------------------------------------------

Binding Signature of Contractor	---------------------------------------------------------------

ANNEXURE-I

Undertaking to be given by the Company/ Partnership Firm/ Contractor along with the Tender

I, _______________________________________________________ representing the Company / Partnership Firm/ Contractor responding to the bid invitation by the APTRANSCO/ APEPDCL/ APSPDCL/ APNPDCL/ APCPDCL vide Specification No. _____________________ hereby sincerely and solemnly affirm and state as follows:

(Strike out that which is not applicable)

a)	That myself or any of the representatives of my company/ firm do not have any relatives as defined in the appended Annexure-III in the APTRANSCO/ DISCOM.

(or)

b)	That the following officers/ employees of the APTRANSCO/ DISCOM are related to me and to the representatives of my company / firm and their status in the APTRANSCO/ DISCOMs is as under.

| S.No. | Name of the officer/ employee | Designation and place of working | APTRANSCO/ DISCOM | Relationship |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |

It is certified that the information furnished above is true to the best of my knowledge and belief. It is hereby undertaken that in the event of the above information found to be false or incorrect at a later date, the APTRANSCO/ DISCOM is entitled to terminate the contract/ agreement entered into besides recovering damages as may be found necessary, with due notice.

Signature of the authorized representative

ANNEXURE-II

Declaration to be given by the  Company/ Partnership Firm/ Contractor at the time of entering into agreement with APTRANSCO/ DISCOMs.

(Strike out that which is not applicable)

a)	I declare that myself or any of the representatives of my company/ firm do not have any relatives as defined in the appended Annexure-III in the APTRANSCO/ DISCOM.

(or)

b)	That the following officers/ employees of the APTRANSCO/ DISCOM are related to me and to the representatives of my company / firm as mentioned here under.

| S.No. | Name of the officer/ employee | Designation and place of working | APTRANSCO/ DISCOM | Relationship |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |

It is certified that the information furnished above is true to the best of my knowledge and belief. It is hereby undertaken that in the event of the above information found to be false at a later date, the APTRANSCO/ DISCOM is entitled to terminate the contract/ agreement entered into besides recovering damages as may be found necessary, with due notice.

Signature of the authorized representative

ANNEXURE-III

List of Relatives:

1)	Father					14)	Daughter’s Husband

2)	Mother (including Step Mother)	15)	 Daughter’s Son

3)	Son (including Step Son)		16)	Daughter’s Son’s Wife

4)	Son’s wife				17)	Daughter’s Daughter

5)	Daughter (including Step Daughter)	18)	Daughter’s Daughter’s Husband

6)	Father’s Mother			19)	Brother (including Step Brother)

7)	Father’s Father			20)	Brother’s Wife

8)	Mother’s Father			21)	Sister (including Step Sister)

9)	Mother’s Mother			22)	Sister’s Husband

10)	Son’s Son 				23)	Son’s Wife’s Father 	and

their

11)	Son’s Son’s Wife			24)	Son’s Wife’s Mother	siblings

12)	Son’s Daughter  			25)	Daughter’s Husband’s Father

and their siblings

13)	Son’s Dauther’s Husband		26)	Daughter’s Husband’s Mother

SECTION 3

CONDITIONS OF CONTRACT

CONDITIONS OF CONTRACT

TABLE OF CONTENTS

| A. GENERAL |  | C. QUALITY CONTROL |  |
| --- | --- | --- | --- |
| 1. Definitions |  | 31. Identifying Defects |  |
| 2. Interpretation |  | 32. Tests |  |
| 3. Language and Law |  | 33. Correction of Defects |  |
| 4. Engineer’s Decisions |  | 34. Uncorrected Defects |  |
| 5. Delegation |  |  |  |
| 6. Communications |  |  |  |
| 7. Subcontracting |  | D. COST CONTROL |  |
| 8. Other Contractors |  | 35. Bill of Quantities |  |
| 9. Personnel |  | 36. Changes in the Quantities |  |
| 10. Employer’s & Contractor’s Risks |  | 37. Variations |  |
| 11. Employer’s Risks |  | 38. Payments for Variations |  |
| 12. Contractor’s Risks |  | 39. Cash Flow Forecasts |  |
| 13. Insurance |  | 40. payment Certificates |  |
| 14. Site Investigation Reports |  | 41. payments |  |
| 15. Queries about the Contract Data |  | 42. Compensation Events 43. Tax |  |
| 16. Contractor to Construct the Works |  | 44. Currencies 45. Price Adjustments |  |
| 17. The Works to be completed by the Intended Completion Date |  | 46. Retention 47. Liquidated Damages |  |
| 18. Approval by the Engineer |  | 48. Advance Payment |  |
| 19. Safety |  |  |  |
| 20. Discoveries |  | 49. Securities |  |
| 21. possession of the Site |  |  |  |
| 22. Access to the Site |  | 50. Cost of Repairs |  |
| 23. Instructions |  |  |  |
| 24. Disputes |  |  |  |
| 25. procedure for Disputes |  | E. FINISHING THE CONTRACT |  |
|  |  | 51. Completion 52. Taking Over |  |
| B. TIME CONTROL |  | 53. Final Account |  |
| 26. program |  | 54. Operating and Maintenance Manuals |  |
| 27. Extension of the Intended Completion Date |  | 55. Termination 56. Payment upon Termination |  |
|  |  | 57. Property |  |
| 28. Delays Ordered by the Meetings |  | 58. Release of Performance |  |
| 29. Management Meetings |  | 59. Suspension of Loan or Credit by REC |  |
| 30. Early Warning |  | F. SPECIAL CONDITIONS CONTRACT |  |

CONDITIONS OF CONTRACT

##### GENERAL

1.   DEFINITIONS

  - Terms which are defined in the Contract Data are also defined in the Conditions of contract but keep their defined meanings.  Capital initials are used to identify defined terms.

Bill of Quantities means the priced and completed Bill of quantities forming part of the Bid.

Compensation Events are those defined in Clause 42 hereunder.

The Completion Date is the date of completion of the Works as certified by the Engineer in accordance with Sub Clause 51.1

The Contract is the contract between the Employer and the Contractor to execute, complete and maintain the Works.  It consists of the documents listed in Clause 2.3 below.

The Contract Data defines the documents and other information, which comprise the Contract.

The Contractor is a person or corporate body whose Bid to carry out the Works has been accepted by the Employer.

The Contractor’s Bid is the completed Bidding documents submitted by the Contractor to the Employer.

The Contract Price is the price stated in the Letter of Acceptance and thereafter as adjusted in accordance with the provisions of the Contract.

Days are calendar days; months are calendar months.

A defect is any part of the Works not completed in accordance with the Contract.

The Defects Liability period is the period named in the Contract Data and calculated from the Completion Date.

The Employer is the party who will employ the Contractor to carry out the Works.

The Engineer is the person named in the Contract Data (or any other competent person appointed and notified to the contractor to act in replacement of the Engineer) who is responsible for supervising the Contractor, administering the Contract, certifying payments due to the Contractor, issuing and valuing variations to the contract, awarding extensions of time, and valuing the Compensation Events.

Equipment is the Contractor’s machinery and vehicles brought temporarily to the Site to construct the Works.

The initial Contract Price is the Contract Price listed in the Employer’s Letter of Acceptance.

The Intended Completion Date is the date on which it is intended that the Contractor shall complete the Works.  The Intended Completion Date is specified in the Contract Data.  The Intended Completion Date may be revised only by the Engineer by issuing an extension of time.

Materials are all supplies, including consumables, used by the contractor for incorporation in the Works.

Plant is any integral part of the Works, which is to have a mechanical, electrical, electronic or chemical or biological function.

The Site is the area defined as such in the Contract Data.

Site Investigations Reports are those which were included in the Bidding documents and are factual interpretative reports about the surface and sub-surface conditions at the site.

Specifications mean the Specification of the Works included in the Contract and any modification or addition made or approves by the Engineer.

The Start Date is given in the Contract Data.  It is the date when the Contractor shall commence execution of the works.  It does not necessarily coincide with any of the Site Possession Dates.

A Subcontractor is a person or corporate body who has a Contract with the Contractor to carry out a part of the work in the Contract which includes work on the Site.

Temporary Works are works designed, constructed, installed, and removed by the Contractor, which are needed for construction or installation of the Works.

A Variation is an instruction given by the Engineer, which varies the Works.

The Works are what the Contract requires the contractor to construct, install, and turn over to the Employer, as defined in the Contract Data.

2.   INTERPRETATION

  - In interpreting these Conditions of Contract, singular also means plural, male           also means female or neuter, and the other way around.  Headings have no           significance.  Words have their normal meaning under the language of the            Contract unless specifically defined.  The Engineer will provide instructions            clarifying queries about the Conditions of Contract.

  - If sectional completion is specified in the Contract Data, references in the              Conditions of Contract to the Works, the Completion Date, and the Intended            Completion Date apply to any Section of the works (other than references to the Completion Date and Intended Completion date for the whole of the Works).

  - The documents forming the Contract shall be interpreted in the following order of priority:

- Agreement

- Letter of Acceptance, notice to proceed with the works.

- Contractor’s Bid

- Contract Data

- Conditions of Contract

- Specifications

- Drawings

- Bill of quantities and

- Any other document listed in the Contract Data as forming part of the Contract.

3.  LANGUAGE AND LAW

  - The language of the Contract and the law governing the Contract are stated in the Contract Data.

4.   ENGINEERS DECISIONS

4.1	Except where otherwise specifically stated, the Engineer will decide contractual matters between the Employer and the Contractor in the role representing the Employer.

5.   DELEGATION

  - The Engineer may delegate any of his duties and responsibilities to other people except to the Adjudicator after notifying the Contractor and may cancel any delegation after notifying the contractor.

- COMMUNICATIONS

  - Communications between parties which are referred to in the conditions are effective only when in writing.  A notice shall be effective only when it is delivered (in terms of Indian Contract Act).

7.   SUBCONTRACTING

7.1	The Contractor subcontract  with the approval of the Engineer but may not assign the Contract without the approval of the Employer in writing.  Subcontracting does not alter the Contractor’s obligations.

8.   OTHER CONTRACTORS

8.1	The Contractor shall cooperate and share the Site with other contractors, public authorities, utilities, and the Employer between the dates given in the Schedule of Other Contractors.  The Contractor shall as referred in the Contract Data, also provide facilities and services for them as described in the Schedule.  The employer may modify the schedule of other contractor and shall notify the contractor of any such modification.

9.   PERSONNEL

  - The Contractor shall employ the key personnel named in the Schedule of Key Personnel as referred to in the Contract Data to carry out the functions stated in the Schedule to other personnel approved by the Engineer.  The Engineer will approve any purposed replacement of Key personnel only if their qualifications, abilities, and relevant experience are substantially equal to or better than those of the personnel listed in the Schedule.

  - If the Engineer asks the Contractor to remove a person who is a member of the Contractor’s staff or his work force stating the reasons the Contractor shall ensure that the person leaves the site within seven days and has no further connection with the work in the Contract.

- EMPLOYER’S AND CONTRACTORS RISKS

10.1   The Employer carries the risks which this Contract states are Employer’s risks, and the Contractor carries the risks which this Contract states are Contractor’s risks.

- EMPLOYER’S RISKS

  - The Employer is responsible for the exceptional risks which are (a) in so far as they directly affect the execution of the Works in the Employer’s country, the risks of war, hostilities, invasion, act of foreign enemies, rebellion, revolution, insurrection or military or usurped power, civil war, riot commotion or disorder (unless restricted to the Contractor’s employees), and contamination from any nuclear fuel or nuclear waste or radioactive toxic explosive, or (b) a cause due solely to the design of the Works, other than the Contractor’s design.

- CONTRACTOR’S RISKS

  - All risks of loss of or damage to physical property and of personal injury and death which arise during and in consequence of the performance of the Contract other than the excepted risks are the responsibility of the Contractor.

- INSURANCE

  - The Contractor shall provide, in the joint names of the Employer and the Contractor, insurance cover from the start Date to the end of the Defects Liability Period, in the amounts and deductibles stated in the Contract Data for the following events which are due to the Contractor’s risks:

- Loss of or damage to the Works, Plant and Materials;

- Loss of or damage to Equipment

- Loss of or damage of property (except the Work, Plant, Materials and Equipment) in connection with the Contract; and

- Personal injury or death.

  - Policies and certificates for insurances shall be delivered by the Contractor to the Engineer for the Engineer’s approval before the Start Date.  All such insurance shall provide for compensation to be payable in the types and proportions of currencies required to rectify the loss or damage incurred.

  - If the Contractor does not provide any of the policies and certificates required, the Employer may effect the insurance which the Contractor should have provided and recover the premiums the Employer has paid from payments otherwise due to the Contractor or, if no payment is due, the payment of the premiums shall be a debt due.

  - Alterations to the terms of insurance shall not be made without the approval of the Engineer.

  - Both parties shall comply with any conditions of the insurance policies.

- SITE INVESTIGATION REPORTS

  - The Contractor, in preparing the Bid, shall rely on any site Investigation Reports referred to in the Contract Data, supplemented by any information available to  the Bidder.

- QURIES ABOUT THE CONTRACT DATA

  - The Engineer will clarify queries on the Contract Data.

- CONTRACTOR TO CONSTRUCT THE WORKS

  - The Contractor shall construct and install the Works in accordance with the Specifications and Drawings.

- THE WORKS TO BE COMPLETED BY THE INTENDED COMPLETION DATE

  - The Contractor may commence execution of the Works on the Start Date and shall carry out the Works in accordance with the program submitted by the Contractor as updated with the approval of the Engineer, and complete them by the intended completion Date.

- APPROVAL BY THE ENGINEER

  - The Contractor shall submit Specifications and Drawings showing the proposed Temporary Works to the Engineer, who is to approve them if they comply with the Specifications and Drawings.

  - The Contractor shall be responsible for design of Temporary Works.

  - The Engineer’s approval shall not alter the Contractor’s responsibility for design of the Temporary Works.

  - All Drawings prepared by the Contractor for the execution of the temporary or permanent Works are subject to prior approval by the Engineer before their use.

- SAFETY

  - The Contractor shall be responsible for the safety of all activities on the Site.

- DISCOVERIES

  - Anything of historical or other interest or of significant value unexpectedly discovered on the Site is the property of the Employer.  The Contractor is to notify the Engineer of such discoveries and carry out the Engineer’s instructions for dealing with them.

- POSSESSION OF THE SITE

  - The Employer shall give possession of all parts of the Site to the Contractor.  If possession of the part is not given by the date stated in the Contract Data the Employer is deemed to have delayed the start of the relevant activities and this will be Compensation Event.

- ACCESS TO THE SITE

  - The Contractor shall allow the Engineer and any person authorized by the Engineer access to the Site, to any place where work in connection with the Contract is being carried out or is intended to be carried out and to any place where materials or plant are being manufactured/fabricated/assembled for the works.

- INSTRUCTIONS

  - The Contractor shall carry out all instructions of the Engineer which comply with

the applicable laws where the Site is located.

  - The Contractor shall permit the bank to inspect the Contractor’s accounts and records relating to the performance of the Contractor and to have them audited by auditors appointed by the Bank, if so required by the Bank.

- DISPUTES

  - If the Contractor believes that a decision taken by the Engineer was whether outside the authority given to the Engineer by the Contract or that the decision was wrongly taken, the decision shall be referred to the Arbitrator within 14 days of the notification of the Engineer’s decision.

- PROCEDURE FOR  DISPUTES

  - The arbitration shall be conducted in accordance with the arbitration procedure published by the institution named and in the place shown in the Contract Data.

B.TIME CONTROL

- PROGRAM

  - Within the time stated in the Contract Data the Contractor shall submit to the Engineer for approval a program showing the general methods, arrangements, order, and timing for all the activities in the Works along with monthly cash flow forecast.

  - An update of the Program shall be a program showing the actual progress achieved on each activity and the effect of the progress achieved on the timing of the remaining work including any changes to the sequence of the activities.

  - The Contractor shall submit to the Engineer, for approval, an updated program at intervals no longer than the period stated in the Contract Data.  If the Contractor does not submit an updated program within this period, the Engineer may withhold the amount stated in the Contract Data from the next payment certificate and continue to withhold this amount until the next payment after the date on which the overdue program has been submitted.

  - The Engineer’s approval of the Program shall not alter the Contractor’s obligations.  The Contractor may revise the Program and submit it to the Engineer again at any time.  A revised Program is to show the effect of variations and Compensations Events.

- EXTENSION OF THE INTENDED COMPLETION DATE

  - The Engineer shall extend the Intended Completion Date if a Compensation Event occurs or a variation  is issued which makes it impossible for Completion to be achieved by the intended Completion Date without the Contractor taking steps to accelerate the remaining work and which would cause the Contractor to incur additional cost.

  - The Engineer shall decide whether and by how much to extend the Intended Completion Date within 21 days of the Contractor asking the Engineer for a decision upon the effect of a Compensation Event or variation and submitting full supporting information.  If the Contractor has failed to give early warning of a delay or has failed to cooperate in dealing with delay, the delay by this failure shall not be considered in assessing the new intended Completion Date.

- DELAYS ORDERED BY THE MEETINGS

  - The Engineer may instruct the Contractor to delay the start or progress of any activity within the Works.

- MANAGEMENT MEETINGS

  - Either the Engineer or the Contractor may require the other to attend management meeting.  The business of a management meeting shall be to review the plants for remaining work and to deal with matters raised in accordance with the early warning procedure.

  - The Engineer shall record the business of management meetings and is to provide copies of his record to those attending the meeting and to the Employer.  The responsibility of the parties for actions to be taken is to be decided by the Engineer either at the management meeting or after the management meeting and stated in writing to all who attend the meeting.

- EARLY WARNING

  - The Contractor is to warn the Engineer at the earliest opportunity of specific likely future events of circumstances that may adversely affect the quality of the work, increase the Contract Price or delay the execution of works.  The Engineer may require the Contractor to provide an estimate of the expected effect of the future event or circumstance on the Contract Price and Completion Date.  The estimate is to be provided by the Contractor as soon as reasonably possible.

  - The Contractor shall cooperate with the Engineer in making and considering proposals for how the effect of such an event or circumstance can be avoided or reduced by anyone involved in the work and in carrying out any resulting instruction of the Engineer.

C.QUALITY CONTROL

- IDENTIFYING DEFECTS

  - The Engineer shall check the Contractor’s work and notify the Contractor of any Defects that are found.  Such checking shall not affect the Contractor’s responsibilities.  The Engineer may instruct the Contractor to search for a Defect and to uncover and test any work that the Engineer considers may have a Defect.

- TESTS

  - If the Engineer instructs the contractor to carry out a test not specified in the Specification to check whether any work has a Defect and the test shows that it does, the Contractor shall pay for the test and any samples.  If there is no Defect the test shall be a Compensation Event.

- CORRECTION OF DEFECTS

33.1     The Engineer shall give notice to the Contractor of any Defects before the end of the Defects Liability Period, which begins at Completion and is defined in the Contract Data.  The Defects Liability period shall be extended for as long as Defects remain to be corrected.

  - Every time notice of a Defect is given, the Contractor shall correct the notified

Defect within the length of time specified by the Engineer’s notice.

- UNCORRECTED DEFECTS

  - If the Contractor has not corrected a Defect within the time specified in the

Engineer’s notice, the Engineer will assess the cost of having the Defect

corrected, and the Contractor will pay this amount.

D.COST CONTROL

- BILL OF QUANTITIES

  - The Bill of Quantities shall contain items for the construction, installation, testing, and commissioning work to be done by the Contractor.

  - The Bill of Quantities is used to calculate the Contract Price.  The Contractor is paid for the quantity of the work done at the rate in the Bill of Quantities for each item.

- CHANGES IN THE QUANTITIES

  - If the final quantity of the work done differs from the quantity in the Bill of Quantities for the particular item by more than 25 percent provided the change not exceeds 1% of initial Contract Price, the Engineer shall adjust the rate to allow for the change.

  - The Engineer shall not adjust rates from changes in quantities if thereby the initial Contract Price is exceeded by more than 15 percent, except with the Prior approval of the Employer.

  - If requested by the Engineer, the Contractor shall provide the Engineer with a detailed cost break down of any rate in the Bill of Quantities.

- VARIAITONS

  - All variations shall be included in updated program produced by the Contractor.

- PAYMENTS FOR VARIATIONS

  - The Contractor shall provide the Engineer with a quotation for carrying out the Variation when requested to do so by the Engineer.  The Engineer shall assess the quotation, which shall be given within seven days of the request or within any longer period stated by the Engineer and before the Variation is ordered.

38.2	If the work in the Variation corresponds with an item description in the Bill of Quantities and if, in the opinion of the Engineer, the quantity of work above the limit stated in Sub Clause 36.1 or the timings of its execution do not cause the cost per unit of quantity the rate in the Bill of Quantities shall be used to calculate the value of the Variation.  If the cost per unit of quantity changes, or if the nature or timing of the work in the Variation does not correspond with items in the Bill of Quantities, the quotation by the Contractor shall be in the form of new rates for the relevant items of work.

38.3	If the Contractor’s quotation is unreasonable, the Engineer may order the variation and make a change to the Contract Price, which shall be based on Engineer’s own forecast of the effects of the Variation on the Contractor’s costs.

  - If the Engineer decides that the urgency of varying the work would prevent a quotation being given and considered without delaying the work, no quotation shall be given and the Variation shall be treated as Compensation Event.

- CASH FLOW FORECASTS

  - When the Program is updated, the Contractor is to provide the Engineer with an updated cash flow forecast.

- PAYMENT CERTIFICATES

  - The Contractor shall submit to the Engineer monthly statements of the estimated value of work completed less the cumulative amount certified previously.

  - The Engineer shall check the Contractor’s monthly statement within 14 days and certify the amount to paid to the Contractor after taking into account any credit or debit for the month in question in respect of materials for the works in the relevant amounts and under conditions set forth in sub-clause 48 (3) of the Contract Data (Secured Advance).

  - The value of work executed shall be determined by the Engineer.

  - The value of work executed shall comprise the value of the quantities of the items in the Bill of Quantities completed.

  - The value of work executed shall include the valuation of Variations and Compensation Events.

  - The Engineer may exclude any item certified in a previous certificate or reduce the proportion of any item previously certified in any certificate in the light of later information.

- PAYMENTS

  - Payments shall be adjusted for deductions for advance payments, retention and other recoveries in terms of the contract and deduction at source of taxes as applicable under the law.  The Employer shall pay the Contractor the amounts certified by the Engineer within 60 days of the date of each certificate.

41.2	Items of the Works for which no rate or price has been entered it will not be paid for by the Employer and shall be deemed covered by other rates and prices in the Contract.

- COMPENSATION EVENTS

  - The following are Compensation Events unless they are caused by the Contractor:

- The Employer does not give access to a part of the Site by the Site Possession Date stated in the Contract Data.

- The Employer modifies the schedule of other contractors in a way, which effects the work of the contractor under the contract.

- The Engineer orders a delay or does not issue drawings, specifications or instructions required for execution of works on time.

- The Engineer instructs the Contractor to uncover or to carry out additional tests upon work, which is then found to have no Defects.

- The Engineer unreasonably does not approve for a subcontract to be let.

(f)	Ground conditions are substantially more adverse than could reasonably have been assumed before issuance of Letter of Acceptance from the information issued to Bidders (including the Site Investigation Reports), from information available publicly and from a visual inspection of the Site.

- The Employer gives an instruction for dealing with an unforeseen condition, caused by the Employer, or addition works required for safety or other reasons.

- Other contractors, public authorities, utilities or the Employer does not work within the dates and other constraints stated in the Contract, and they cause delay or extra cost to the Contractor.

- The effect on the Contractor of any of the Employer’s Risks.

- The Engineer unreasonably delays issuing a Certificate of Completion.

(k).	Other Compensation Events listed in the Contract Data or mentioned in the Contract.

  - If a Compensation Event would cause additional cost or would prevent the work being completed before the intended Completion Date, the Contract Price shall be increased and/or the Intended Completion Date is extended.  The Engineer shall decide whether and by how much the Contract Price shall be increased and whether any by how much the Intended Completion Date shall be extended.

42.3	As soon as information demonstrating the effect of each Compensation Event upon the Contractor’s forecast cost has been provided by the Contractor, it is to be assessed by the Engineer and the Contract Price shall be adjusted accordingly.  If the Contractor’s forecast is deemed unreasonable, the Engineer shall adjust the Contract Price based on Engineer’s own forecast.  The Engineer will assume that the Contractor will react competently and promptly to the event.

  - The Contractor shall not be entitled to compensation to the extent the Employer’s interest are adversely affected by the Contractor not having given early warning or not having cooperated with the Engineer.

- TAX

43.1	The rates quoted by the Contractor shall be deemed to be inclusive of the sales and other taxes that the Contractor will have to pay for performance of this Contract.  The Employer will perform such duties in regard to the deduction of such taxes at source as per applicable law.

- CURRENCIES

  - All payments shall be made in Indian Rupees.

45	PRICE ADJUSTMENT - DELETED

46	RETENTION - DELETED

47	LIQUIDATED DAMAGES

47.1	The Contractor shall pay liquidated damages to the Employer at the rate per day stated in the Contract Data for each day that the Completion Date is later than the intended Completion Date (for the whole of the works or milestone as stated in the contract Data).  The total amount of liquidated damages shall not exceed the amount defined in the Contract Data.  The Employer may deduct liquidated damages from payments due to the Contractor.  Payment of liquidated damages does not affect the Contractor’s liabilities.

47.2	If the Intended Completion Date is extended after liquidated damages have been paid, the Engineer shall correct any overpayment of liquidated damages by the Contractor by adjusting the next payment certificate.  The Contractor shall be paid interest on the over payment calculated from the date of payment to the date of repayment at the rates specified in Sub Clause 41.1.

48	ADVANCE PAYMENT - DELETED

49	SECURITIES

  - The Performance Security (including additional security for unbalanced bids) shall be provided to the Employer no later than the date specified in the Letter of Acceptance and shall be issued in an amount and form and by a bank or surety acceptable to the Employer, and denominated in India Rupees.  The Performance Security shall be valued until a date 28 days from the date of expiry of Defects Liability period and the additional security for unbalanced bids shall be valid until a date 28days from the date of issue of the certificate of completion.

- COST OF REPAIRS

  - Loss of damage to the Works or Materials to be incorporated in the Works between the Start Date and the end of Defects correction periods shall be remedied by the Contractor at the Contractor’s cost if the loss or damage arises from the Contractor’s acts or omissions.

E. FINISHING THE CONTRACT

- COMPLETION

51.1	The Contractor shall request the Engineer to issue a Certificate of Completion of the Works and the Engineer will do so upon deciding that the work is completed.

- TAKING OVER

  - The Employer shall take over the Site and the Works within seven days of the Engineer issuing a certificate of completion.

- FINAL ACCOUNT

  - The Contractor shall supply to the Engineer a detailed account of the total amount that the Contractor considers payable under the contract before the end of the Defects Liability Period.  The Engineer shall issue a Defect Liability Certificate and certify any final payment that is due to the Contractor within 56 days of receiving the Contractor’s account if it is correct and complete.  If it is not, the Engineer shall issue within 56 days a schedule that states that scope of the corrections or additions that are necessary.  If the Final Account is still unsatisfactory after it has been resubmitted, the Engineer shall decide on the amount payable to the Contractor and issue a payment certificate, within 56 days of receiving the Contractor’s revised account.

- OPERATING AND MAINTENANCE MANUALS

  - If “as built” Drawings and/or operating and maintenance manuals are required, the Contractor shall supply them by the dates stated in the Contract Data.

  - If the Contractor does not supply the Drawings and/or manuals by the dates stated in the Contract Data, or they do not receive the Engineer’s approval, the Engineer shall withhold the amount stated in the Contract Data from payment due tot he Contractor.

- TERMINATION

  - The Employer or the Contractor may terminate the Contract if the other party causes a fundamental breach of the Contract.

  - Fundamental breaches of Contract include, but shall not be limited to the following.

- The Contractor stops work for 28 days when no stoppage of work is shown on the current program and the stoppage has not been authorized by the Engineer.

- The Engineer instructs the Contractor to delay the progress of the Works and the instruction is not withdrawn within 28 days.

- The Employer or the Contractor is made bankrupt or goes into liquidation other than for reconstruction or amalgamation.

- A payment certified by the Engineer is not paid by the Employer to the Contractor within 120 days of the date of the Engineer’s certificate:

- The Engineer gives Notice that failure to correct a particular Defect is a fundamental breach of Contract and the Contractor fails to correct it within a reasonable period of time determined by the Engineer.

- The Contractor does not maintain a security which is required;

- The Contractor has delayed the completion of works by the number of days for which the maximum amount of liquidated damages can be paid as defined in the Contract data; and

- If the Contractor, in the judgement of the Employer has engaged in corrupt or fraudulent practices in competing for or in the executing the Contract.

For the purpose of this paragraph: “corrupt practice” means the offering, giving receiving or soliciting of any thing of value to influence the action of a public official in the procurement process or in contract execution.  “Fraudulent Practice” means a misrepresentation of facts in order to influence a procurement process or the execution of a contract to the detriment of the Borrower, and includes collusive practice among Bidders (prior to or after bid submission) designed to establish bid prices at artificial non-competitive levels and to deprive the Borrower of the benefits of free and open competition.

  - When either party to the Contract gives notices of a breach of contract to the

Engineer for a cause other than those listed under Sub Clause 55.2 above, the Engineer shall decide whether the breach is fundamental or not.

  - Notwithstanding the above, the Employer may terminate the Contract for

convenience.

  - If the Contract is terminated the Contractor shall stop work immediately, make the Site safe and secure and leave the Site as soon as reasonably possible.

- PAYMENT UPON TERMINATION

56.1	If the Contract is terminated because of a fundamental breach of Contract by the Contractor, the Engineer shall issue a certificate for the value of the work done  less advance payments received up to the date of the issue of the certificate, less other recoveries due in terms of the contract, less taxes due to the deducted at source as per applicable law and less the percentage to apply to the work not  completed as indicated in the Contract Data.  Additional Liquidated Damages shall not apply.  If the total amount due to the Employer exceeds any payment due to the Contractor the differences shall be a debt payable to the Employer.

56.2	If the Contract is terminated at the Employer’s convenience or because of a fundamental breach of contract by the Employer, the Engineer shall issue a certificate for the value of the work done, the reasonable cost of removal of Equipment, repatriation of the Contractor’s personnel employed solely on the works, and the Contractor’s costs of protecting and securing the Works and less advance payments received up to the date of the Certificate, less other recoveries due in terms of the contract and less taxes due to be deducted at source as per applicable law.

- PROPERTY

  - All materials on the Site, Plant, Equipment, Temporary Works and Works are deemed to be the property of the Employer, if the Contract is terminated because of a Contractor’s default.

- RELEASE FROM PERFORMANCE

  - If the Contract is frustrated by the outbreak of war or by another event entirely outside the control of either the Employer or the Contractor the Engineer shall certify that the Contract has been frustrated.  The Contractor shall make the Site safe and stop work as quickly as possible after receiving this certificate and shall be paid for all work carried our before receiving it and for any work carried our afterwards to which commitment was made.

- SUSPENSION OF LOAN OR CREDIT BY REC

  - In the event that the REC suspends the Loan or Credit to the Employer, from which part of the payments to the Contractor are being made:

(a)	The Employer is obligated to notify the Contractor of such suspension within 7 days of having received the REC’s suspension notice.

F. SPECIAL CONDITIONS OF CONTRACT

TABLE OF CONTENTS

| S. NO. |  |  |
| --- | --- | --- |
| 1. | DESCRIPTION |  |
| 1.1A | RESPONSIBILITY FOR EXECUTION OF THE CONTRACT |  |
| 1.1B | NOTICES |  |
| 2. | WORKING HOURS |  |
| 3. | EXTRA SHIFTS AND OVER TIME WORK |  |
| 4. | ACCIDENTS |  |
| 5. | INSURANCE FOR MATERIALS SUPPLIED BY BOARD |  |
| 5.1 | INDEMNITIES |  |
| 6. | LICENSE |  |
| 7. | TRANSPORT ARRANGEMENT |  |
| 8. | MACHINERY TOOLS AND TACKLES |  |
| 9. | SAFETY PRECAUTIONS |  |
| 10. | FIRE PRECAUTIONS |  |
| 11. | WORKING AREA AND CLEANLINESS |  |
| 12. | SITE DISCIPLINE |  |
| 13. | SITE OFFICE AND SITE STORES |  |
| 14. | APPROVAL OF INSTALLATION BY GOVERNMENT AUTHORITIES (CEIG) |  |
| 15. | MEASUREMENT OR WORK |  |
| 16. | INCOME TAX |  |
| 17. | TERMINATION OF CONTRACT FOR BOARDS CONVENIENCE |  |
| 18. | LABOUR |  |
| 19. | COMPLIANCE WITH LABOUR REGULATIONS |  |
| 20. | ARBITRATION |  |
| 21. | RESPONSIBILITY FOR EXECUTION OF THE CONTRACT |  |

F. SPECIAL CONDITIONS OF CONTRACT

- DESCRIPTION

The Contractor shall, at all times during the continuance of the contract, comply fully with all existing Acts, regulations and bye laws including all statutory amendments and reenactments of State or Central Government and other local authorities and any other  enactments, notifications and acts that may be passed in future either by the State or the Central government or local authority, including Indian Workmen’s Compensation Act, 1923.  Contract Labour (Regulation and Abolition) Act 1970, the Child Labour Prohibition and Regulation Act 1986, and Equal Remuneration Act 1976, Factories Act, Minimum Wages Act 1948, Provident Fund Regulations, Employees Provident Fund Act 1952 EPF Act 1996 and related acts passed from time to time.  Schemes made under the Same Act the Buildings and other construction workers (Regulation of Employment and condition of Service) Act 1996, the Cess Act 1996 and also applicable Labour Regulations, Health and Sanitary Arrangement for Workmen, Insurance and other benefits and shall keep Employer indemnified in case any action is commenced by Competent authorities for contravention by the Contractor.

If the Employer is caused to pay or reimburse, such amounts as may be necessary to cause or observe, or for non-observance of the provisions stipulated above on the part of the Contractor, the Engineer shall have the right to deduct from any amounts due to the Contractor, his amount of Performance Security or recover from the Contractor personally any sum required or estimated to be required for making good the loss or damage suffered by the employer, responsibility in connection with the employees of the contractor, who shall, in no case, be treated as the employees of the Employer at any point of time.

1.1 A	RESPONSIBILITY FOR EXECUTION OF THE CONTRACT (CLAUSE 16 OF S.C.C.)

The Contractor shall carry out the entire work according to sound engineering practices.  The responsibility lies with the Contractor for the proper execution of the erection work according to existing laws and bye laws at the time of contract execution.  The Contractor shall confirm in respects to the requirements to CEIG (Chief Electrical Inspector to Government of A. P.) as and when required by them.  However, the Contractor shall have to follow the instructions of the Employer or his authorized representative in respect of the following.

- Progress reports to be submitted from time to time.

- Progress and completion of the work according to the time schedule.

- Execution of contract works to the Purchaser’s entire satisfaction.

- Submitting the details regarding the name of the responsible persons for execution of this contract.

- Preparing, submission and getting approval of the Complete electrical system of the power plant including the switch yard.

1.1.B.	NOTICES:

    - All Certificates, notices or written orders to be given by the Employer to the Contractor under the terms of the contract shall be served by sending by post to or delivering the same to Contractor’s principal place of business, or such other address as the Contractor shall nominate for this purpose.

    - All notices to be given to the APSPDCL or to the Engineer under the terms of the Contract shall be served by sending by post or delivering the same to the respective addressee nominated for that purpose.

The Employer’s address is

Chief General Manager (Projects), Southern Power Distribution Company of A.P. Limited,

D.No.19-3-13 (M), Renigunta Road, Tirupati - 517501

The Engineer’s address is

Divisional Engineer (Construction)

O/o Superintending Engineer (Operation)									APSPDCL

District.

- WORKING HOURS (CLAUSE 12 OF G.C.C.)

Before commencement of work, the contractor shall inform in writing, the normal working hours for his staff and workers.  These hours be as far as possible in consonance with the Employer’s working hours for better coordination.

All the staff and workers should positively leave the site premises after these hours, except for authorized watch and ward personnel, approved by the employer.

- EXTRA SHIFT & OVERTIME WORK (CLAUSE 12 OF G.C.C.)

At the commencement of work, the Contractor shall arrange for a general shift, as per working hours.

If, at a later date the employer feels that extra shift should be started to complete work allotted to the contractor within the time stipulated or to make up for any past delays.  The contractor shall arrangement for.

- ACCIDENTS (CLAUSE 12 OF G.C.C.)

The employer will not be responsible for any damages or compensation payable inconsequence of an accident or injuries to any of the Contractor’s personnel or any third party.

The contractor shall insure at his cost-against any such eventuality as per rules in force and submit the documentary evidence of the Insurance Policy taken, positively prior to commencement of work at site and should keep policy valid by paying premium and other changes will handing over of the plant.

In case of any accidents at or near the site in connection with the execution of work, the contractor shall with in 24 hours, make a detailed report of accident and submit the same to the purchaser in the form provided by the purchaser.

The contractor shall also report such accidents to the competent authority as laid down by the existing rules and regulations and inform the Employer regarding the same.

- INSURANCE FOR MATERIALS SUPPLIED BY APSPDCL (CLAUSE 13 OF G.C.C.)

The Contractor shall insure in the name of the APSPDCL for the amount equal to the value of material supplied to him by the APSPDCL against loss or damage for the period from the time of taking over the materials from the APSPDCL to the date of issue of completion certificate.  The value of the policy shall be enhanced from time to time depending upon the value of the APSPDCL materials taken over.

5.1	INDEMNITIES

The contractor is liable for and indemnifies the APSPDCL against losses, expenses and claims for loss or damage to physical property, personal injury and death caused by his own acts or omissions.

  - The contractor claiming indemnity is to take all reasonable steps to mitigate the lower damage will occur.

5.3	the contractor indemnifies the APSPDCL against claims to damages caused by the movements of his equipment or temporary works.

  - The Contractor shall submit an “Indemnity Bond” to the APSPDCL incorporating the above points before taking up the execution of the work.

6.	LIECENCE (CLALUSE 16 OF G.C.C.)

The contractor or his sub-contractor shall have valid contractor’s license from Electrical Inspector of A. P. State, and he shall maintain its validity for the complete duration of the contract.

- TRANSPORT ARRANGEMENT (CLAUSE 17 OF G.C.C.)

The contractor shall make the transport arrangement at his cost for his staff and workers to site.

- MACHINERY, TOOLS & TACKLES (CLAUSE 17 OF G.C.C.)

The Contractor shall provide the required machinery/equipment, accessories, necessary tools and tackles, instruments, and all the normal consumable materials required for the satisfactory execution of this contract.  The Contractor shall arrange for cranes for unloading and erection purpose, if required.

Gate Pass for Materials:

All tools, tackles, construction materials, welding materials etc., will be taken inside the site limits only after registration with security personnel.  Also any material will be taken out only on valid gate pass issued by purchaser’s representative after checking the proper “IN” gate passes.  The contractor shall have to preserve the “IN” gate passes obtained from security when every /any material is route inside the site to enable taking back the balance/excess materials, Tools and Tackles after completion of works.

- SAFETY PRECAUTIONS (CLAUSE 19 OF G.C.C.)

All the safety measures to avoid accidents shall be followed strictly in accordance with the safety rules and regulation laid down by the government authorities.

The Contractor shall take all safety precautions and shall provide proper scaffolding, life-belts, ladder shock proof helmets, etc. to avoid accidents and to ensure safety, of not only his personnel but also the safety of the staff and workers of other contractors working at the same site.

The contractor shall take necessary precautions to ensure that no part of the building/structure damage or disfigured due to negligence on his part while carrying out the work.  In case of excess damage, the same shall be made good by the contractor immediately at his own cost.

Re-commissioning on energized equipment shall be carried out with proper safety permits issued by the Purchaser/Competent authorities.  When required to work at heights or at hazardous location areas, the contractor shall carryout the same with utmost care and all safety precautions.

- FIRE PRECAUTIONS (CLAUSE 19 OF G.C.C.)

The contractor shall strictly instruct his site staff and workers to abide by the regulations in force at the site regarding all precautions to be taken to avoid fire hazards.

- WORKING AREA & CLEANLINESS (CLAUSE 21 OF G.C.C.)

The Contractor shall keep the site of work in a clean and sanitary condition.  After the completion of the entire work, the contractor shall arrange to remove all the temporary structures, surplus materials, dirt, debris, etc. from the site and finished work shall be handed over the employer in a clean and complete shape.

- SITE DISCIPLINE (CLAUSE OF G.C.C.)

Strict discipline shall be observed by all the contractor’s personnel inside the premises of the site.  The contractor and his personnel shall abide by all the rules and regulations of the Employer, Disciplinary action shall be taken against the Contractor/his personnel and their services liable to be terminated, if found quarrelling/ violating the rules.

- SITE OFFICE & SITE STORES (CLAUSE 21 OF G.C.C.)

The Contractor will make necessary arrangements for erection of his site office and site stores after getting written permission from the employer to erect such temporary structure at his own cost.  Temporary power supply will be provided at one point at the nearest switch room. The power consumption charges will have to be borne by the Contractor.  However, non-availability of the Crane does not leave the contractor off his responsibilities.  The contractor is permitted to make use of water source available in any sub-station sites for construction purpose.

Transport of water from the source to the working areas will be contractor’s responsibility.

- APPROVAL OF INSTALLATION BY GOVERNMENT AUTHORITIES (CEIG) (CLAUSE 51OF G.C.C.)

Wherever approval of government authorities is required, as per existing rules and regulations, the Contractor shall obtain the same.

- MEASUREMENT (CLAUSE 40 OF G.C.C.)

The Engineer shall, except as otherwise stated ascertain and determine by measurement the value in terms of the contract of work done in accordance with the contract.  He shall, when required any part or parts of the works to be measured, give notice to the contractor’s authorised agent or representative, who shall forth with attend or send a qualified agent to assist the Engineer or the Engineer’s Representative in making such measurement, and shall furnish all particulars required by either of them.  Should the contractor not attend or neglect or omit to send such agent, then the measurement of the work.  For the purpose of measuring such permanent work as is to be measured by records and drawings, the Engineer’s representative shall prepare records and drawings month by month of such work and the contractor, as and when called upon to do so in writing, shall within fourteen days, attend to examine and agree such records and drawings, they shall be taken to be correct.  If, after examination of such records, and drawings, they shall nevertheless be taken to be correct, unless the contractor shall, within Fourteen days of such examination, lodge with the Engineer’s Representative, for decision by the Engineer, notice in writing of the respects in which such records and drawings are claimed by him to be incorrect.  Payments will be made to the contractor by cheque at monthly intervals.  The contractor shall submit his hills for work accomplished and measured by Engineer on or before the last day of month.

- INCOME TAX (CLAUSE 43 OF G.C.C.)

- Deductions will be made towards Income Tax at source by the APSPDCL as directed by Income Tax Department.

b)	The Contractor’s staff, personnel and labour will be liable to pay personnel income taxes in India in respect of such of their salaries and wages as are chargeable under the laws and regulations for the time being in force, and the contractor shall perform such duties in regard to such deductions there of as may be imposed on him by such laws and regulations.

17.	TERMINATION OF CONTRACT FOR APSPDCL CONVENIECE (CLAUSE 55.4 OF G.C.C.)

The APSPDCL shall be entitled to terminate this contract at any time for the APSPDCL convenience after giving 30 days prior notice to the contractor with a copy to the Engineer.

18       LABOUR

The Contractor shall, unless otherwise provided in the contract, make his own arrangements, for the engagements of all staff and labour, local, or other, and for their payment, housing, feeding and transport.

The Contractor shall, if required by the Engineer, deliver to the Engineer a return in detail, in such form and at such intervals as the Engineer may prescribe showing the staff and the numbers of the several classes of labour from time to time employed by the Contractor on the Site and such information respecting Contractor’s Equipment as the Engineer may require.

- COMPLIANCE WITH LABOUR REGULATIONS

During continuance of the Contract, the Contractor and his sub contractors shall abide at all times by all existing labour enactment’s and rules made thereunder, regulations, notifications and bye laws of the State or Central Government or local authority and any other labour law (including rules), regulations, bye laws that may be passed or notification that may be issued under any labour law in future either by the State or the Central Government or the local authority.  Salient features of some of the major labour laws that are applicable to construction industry are given below.  The Contractor shall keep the Employer indemnified in case any action is taken against the Employer by the Competent authority on account of contravention of any of the provisions of any Act or rules made thereunder, regulations or notifications including amendments.  If the Employer is caused to pay or reimburse, such amounts as may be necessary to cause or observe, or for non-observance of the provisions stipulated in the notifications/bye laws/Acts/Rules /regulations including amendments, if any, on the part of the Contractor, the Engineer/Employer shall have the right to deduct any money due to the contractor including his amount of performance security.  The Employer/Engineer shall also have right to recover from the Contractor any sum required or estimated to be required for making good the loss or damage suffered by the Employer.

The employees of the Contractor and the Sub-Contractor and the Sub-Contractor in no case shall be treated as the employees of the Employer at any point of time.

SALIENT FEATURES OF SOME MAJOR LABOUR LAWS APPLICABLE TO ESTABLISHMENTS ENGAGED IN BUILDING AND OTHER CONSTRUTION WORK.

- Workmen Compensation Act 1923: - The Act provides for compensation in case of injury by accident arising out of and during the course of employment.

- Payment of Gratuity Act 1972: -  Gratuity is payable to an employee under the Act on satisfaction of certain conditions on separation if an employee has completed 5 years service or more or on death the rate of 15 days wages for every completed year of service.  The Act is applicable to all establishments employing 10 or more employees.

- Employees P. F. and Miscellaneous Provision Act 1952: The Act for monthly contributions by the employer plus workers @10% or 8.33%.  the benefits payable under the Act are:

- Pension or family pension on retirement or death, as the case may be

(ii)  Deposit linked insurance on the death in harness of the worker.

(iii)	Payment  of P. F. accumulation on retirement /death etc.

- Maternity Benefits Act 1951: -The Act provides for leave and some other benefits to women employees in case of confinement or miscarriage etc.

- Contract labour (Regulation &Abolition) Act 1970: - The Act provides for certain welfare measures to be provided b y the contractor to contract labour and in case the Contractor fails to provide, the same are required to be provided, by the principal Employer by Law.  The Principal Employer is required to take Certificate of Registration and the Contractor is required to take license from the designated officer.  The Act is applicable to the establishments or Contractor of Principal Employer if they employ 20 or more contract labour.

- Minimum Wages Act 1948: - The Employer is supposed to pay not less than the Minimum Wages fixed by appropriate Government as per provision of the Act if the employment is a scheduled employment.  Construction of Buildings, Roads, Runways are scheduled employment’s.

- Payment of Wages Act 1936: -  It lays down as to by what date the wages are to be paid, when it will be paid and what deductions can be made from the wages of the workers.

- Equal Remuneration Act 1979: -  The Act provides for payment of equal wages for work of equal nature to Male and Female workers and for not making discrimination against Female employees in the matters of transfers, training and promotions etc.

i)	Payment of Bonus Act 1965: - The Act is applicable to all establishments employing 20 or more employees. The Act provides for payments of annual bonus subject to a minimum of 8.33% of wages and maximum of 20% of wages to employees drawing Rs.3500/- per month or less.  The bonus to be paid to employees getting Rs.2500/- per month or above up to Rs.3500/- per month shall be worked out by taking wages as Rs.2500/- per month only.   The Act does not apply to certain establishments.  The newly set-up establishments are exempted for five years in certain circumstances.  Some of the State Governments have reduced the employment size from 20 to 10 for the purpose of applicability of this Act.

- Industrial Disputes Act 1947: - The Act lays down the machinery and procedure for resolution of Industrial disputes, in what situations or lock-out becomes illegal and what are the requirements of laying off or retrenching the employees or closing down the establishments.

- Industrial Employment (Standing Orders) Act 1946: - It is applicable to all establishments employing 100 or more workmen (employment size reduced by some of the States and Central government to 50).  The Act provides for laying down rules governing the conditions of employment by the Employment on matters provided in the Act and get the same certified by the designated Authority.

l)	Trade Union Act 1926: - The Act lays down the procedure for registration of trade unions of workmen and employers.  The Trade Unions registered under the Act have been given certain immunities from civil and criminal liabilities.

- Child Labour (prohibition & Regulation) Act 1986: - The Act prohibits employment of children below 14 years of age in certain occupations and process and provides for regulation of employment of children in all other occupations and processes.  Employment of Child Labour is prohibited in Building and Construction Industry.

- Inter-State Migrant Workmen’s (Regulation of Employment & Conditions of Service) Act 1979: - The Act is applicable to an establishment which employ 5 or more inter-state migrant workmen through an intermediary (who has recruited workmen in one state for employment in the establishment situated in another state).  The Inter State migrant workmen, in an establishment to which this Act becomes applicable, are required to be provided certain facilities such as housing, medical aid, traveling expenses from home up to the establishment and back, etc.

o)	The Building and Other Construction Workers (Regulation of Employment and Conditions of Service) Act 1996 and the Cess Act of 1996:  All the establishments who carry on any building or other construction work and employs 10 or more workers are covered under this Act.  All such establishments are required to pay cess at the rate not exceeding 2% of the cost of construction as may be modified by the Government.  The Employer of the establishment is required to provide safety measures at the building or construction work and other welfare measures, such as Canteens, First- Aid facilities, Ambulance, Housing accommodations for workers near the work place etc.  The Employer to whom the Act applies has to obtain a registration certificate from the Registering Officer appointed by the Government.

p)	Factories Act 1948: - The Act lays down the procedure for approval at plans before setting up a factory, health and safety provisions, welfare provisions, working hours, annual earned leave and rendering information regarding accidents or dangerous occurrences to designated authorities.  It is applicable to premises employing 10 persons or more with aid of power or 20 or more persons without the aid of power engaged in manufacturing process.

20	ARBITRATION (GCC CLAUSE 25.1)

The Procedure for arbitration will be as laid down Indian Arbitration and conciliation act 1996.

21)	Responsibility for execution of the Contract:

The contractor shall carryout the entire work according to sound Engineering practices. The responsibility lies with the contractor for proper execution of work according to existing loss and bylaws. The contractor shall have to follow the instructions of the Employer or Engineer – In – Charge.

a)	Progress reports shall be furnished fortnightly.

b)	The details of project manager and site supervisors.

c)	Inspection of supports, conductor and other equipment at manufacturer’s site by the Employer.

d)	Approval test certificates before dispatch the material /equipment to site.

e)	Proper storage of  material / equipment.

f)	“As Built” drawings and schedules shall be submitted with in 15 days of completion of the work.

g)	Operating manuals and operating instructions shall be furnished.

SECTION 4

CONTRACT DATA

CONTRACT DATA

Items marked “N/A” do not apply in this Contract.

The following documents are also part of the Contract:

Clause

Reference

- The Schedule of Operating and Maintenance Manuals			(54)

- The Schedule of Other Contractor						(8)

- The Schedule of Key Personnel.							(9)

The above insertions should correspond to the information provided in the Invitation of Bids.

The Employer is

Name:       Chief General Manager/Projects

Address:   Southern Power Distribution Company of A.P Ltd.

D.No.19-3-13 (M), Renigunta Road,

Tirupati.

Name of authorised Representative: Superintending Engineer/Operation /

The Engineer is								(1.1)

Name:	 	Divisional Electrical Engineer (Construction) /

Address:

Name of Authorised Representative: Divisional Engineer, Elect.  Construction

Name 		: ____________________________________  	(1.1)

Address 	: _________________________________________________

The name and identification number of the Contract is Bid No.

___________________________________________________________________

(insert name and number as indicated in the Invitation for Bids (or Pre-qualification, if any). (1.1)

The works consist of _________________________________________

(brief Summary, including relationship to other contracts under the project).

The Start Date shall be Date of Issue or Letter Indent. 			(1.1)

The Intended Completion Date for the whole

Of the Works should comply with the following milestones:			    (17, 27)

Milestone dates:

works to be completed			period from the date of issue of

Notice to proceed with the work.

Milestone i.e. Completion of work			Six months from the start date.

The following documents also part of the Contract:				(2.3)

The Contractor shall submit a revised Program for the Works

Within 30 days of delivery of the Letter of Acceptance.			 (26)

The Site Possession Dates shall be:						 (21)

Within a month after entering into Agreement

The Site is located at		___________________			  (1)

And is defined in drawings on.___________________________

The Defects Liability Period is 12 months from the date of issue of completion

certificate       	(33)

The minimum insurance cover for physical property, injury	 (13)

And death if Five (lakhs) per occurrence with the number of occurrences

Limited to four, After each occurrence, contractor will pay additional premium

Necessary to make insurance valid for four occurrences always.

The Compensation Events:	(42)

The period between program updates shall be 30 days.			(26)

The amount to be withheld for late submission of an updated		(26)

Program shall be Rs.25,000/-

The language of the Contract documents is English				(3)

The law which applies to the Contract is the law of India			(3)

The currency of the Contract is Indian Rupees. 				(44)

Institution whose arbitration procedures shall be used: 			(25)

Arbitration will take place in accordance with Indian Arbitration Conciliation act 1996. 										(25)

100% payment will be made on or after 30 days of completion of the items in all respects

The liquidated damages for whole of the works are

At Rs. 0.05% on the estimated cost per day (amount) per day and that for the milestone are as under: 							(47)

The maximum amount of liquidated damages for the whole of the works	(47)

is ten percent of final contract price.

#### SECTION 5

#### TECHNICAL SPECIFICATIONS

TECHNICAL SPECIFICATIONS

1.	9.1 Mts. & 8.0 Mts. PSCC poles

2.	100 Sq.mm, 55 Sq.mm & 34 Sq.mm AAA Conductor

3.	200 Sq.mm ACSR Conductor

4.	33KV & 11KV Disc Insulators

5.	33KV & 11KV Pin Insulators

6.	AB Switches

a) 33KV AB switch 800 A

b) 11KV AB switch 400 A

c) 11KV AB switch 200 A

7.	33KV & 11KV Lines

8.	Sub-station works

9.	24V Lead Acid Batteries

10.	Erection of Bays

## TECHNICAL SPECIFICATION

## PRESTRESSED CEMENT CONCRETE POLES (9.1 Mts. & 8.0 Mts.)

(PRETENSIONED TYPE)

- Scope

1.1	This specification covers the manufacture and supply, delivery at site of pretensioned prestressed  cement concrete poles as per specifications No. IS : 1343 and 1678 and as amended up to date and including all other relevant standards.

- Design

  - The poles shall be manufactured in accordance with the APSPDCL design & drawing, enclosed.  The poles are designed to withstand the working loads of (a) 280 Kg for 9.1M lengths (b) 200 Kg for 8.0 M length respectively, acting at 0.6 M from top of the poles and the planting depth of the poles being 1.5 M below ground level.  Where the Bidder wants to submit his own design which are economical, the load indicated by the APSPDCL shall be adopted and detailed calculations shall be submitted to the APSPDCL for approval along with his tender.  Otherwise, it shall be construed that the bidder’s prices are for the APSPDCL design only and any subsequent change in design shall be subjected to the approval of APSPDCL, as laid down in this specification and the price shall be reduced by the difference in cost of various ingredients as per the estimated  cost of the same at SSR rates in case of reductions and no extra rates are payable in case of any increase whatsoever.

  - The manufacturing process to be adopted for mass production shall be with the specific prior approval of the APSPDCL.

  - The contactor should supply 6 Nos. of poles in each category of length for testing against design load adopted.  On being found satisfactory, design will be accepted for further production.  In case of failure in tests the firm will have to supply additional 6 Nos. Poles in each category for further tests.

- Materials

    - The properties of the high tensile steel as 6003/1970 along with test certificates shall be verified by the Engineer and approved before commencing manufacture.  In the absence of test reports three samples shall be selected in the presence of the Engineer and tests conducted in stock tested periodically at the cost of the tenderer.

    - The cement used shall conform to IS 269-1976 (Specification for ordinary and low heat Portland cement  for the following minimum requirements.

- Initial setting time Not less than 30 minutes.

- Final setting time Not les than 600 minutes.

- The minimum compressive strength of standard mortar cube with graded sand as per IS : 650-1966 (1st revision ) at 7 days shall be 220 kg./sg.cm)

- 53 Grade cement manufactured by the standard company shall be used in the work.

3.2.2	As far as possible, the cement shall be obtained from one source to minimise variations in  the quality.  A test certificate shall cover each consignment.  Each consignment of cement shall be stocked separately and shall be clearly identified.

3.2.3	Before using a particular batch of cement, a minimum of 3 trial cubes shall be made with aggregate grading as followed for the approved design mix and the average compressive strength results at 7 days shall be determined to assess the suitability of the cement.  Any other suitable quick testing method may be adopted with the approval of the Engineer.

  - Aggregate :

    - For adequate control of concrete, the coarse aggregates shall be classified into two sizes, and the requisite proportions of each size shall be used in making the concrete. Each size of graded aggregates shall be stocked in different storage bins or stock piles and shall be mixed only after the quantity required for each size has been separately weighed. The storage bins or stock piles shall be under cover protected from weather.

    - The quality of the aggregate shall conform to IS 383 – 1970

  - Concrete :

    - The concrete shall be of ‘Controlled’ quality with the nominal maximum size of aggregates limited to 20mm.

    - Two granulometric curves for aggregates shall be plotted by the manufacturer showing the limits of grading according to the types and sizes of the aggregates proposed to be used to achieve the requisite strength of concrete. The curves and the proposed water cement ratio shall be got approved by the Engineer before commencing manufacture. The actual granulometric curves for aggregates used in manufacture shall lie within these limits. To ensure, a compliance with this requirement, the granulometric curves shall be plotted and checked every day before commencement of concreting. Whenever there is change in source or quality of aggregate and cement, fresh granulometric curves shall be plotted and got approved by the Engineer. The water cement ratio should preferably be as low as possible aiming at zero/no slump and should preferably be between 0.33 to 0.37. The moisture content in fine aggregates shall be determined daily and the required quantities of water to be added in the concrete mix shall be determined.

    - The mix design shall be in accordance with the provisions of Clauses 208 to 210 of British Standard code of practice (CP110/1972 and the standard deviation shall be taken as 66N/Sq.mm.)

- Design

  - The strength of the concrete shall be as below :

    - Compressive strength at 28 days: The work test cube crushing strength of the concrete shall not be less than 400 Kg/Sq Cm. The specified strength of the mix to be used in the works is 400 Kg/Sq.Cm. The designed target strength of the mix is 466 Kg/Sq.cm

    - Compressive strength at transfer : The works cube compressive strength at transfer of prestress shall not be less than 200 Kg/Sq.Cm under conventional water curing process.

  - A minimum of 6 test specimens of 15 Cms cubes shall determine the compressive strength of concrete at each stage. The compressive strength  stipulated above shall be based on the lowest cube test result of the 6 test specimens. This shall, however, be relaxed to the second lowest cube test result in case the number of test specimens is increased to a minimum of 12 at each stage.

  - The final working stress in concrete shall be limited as follows

- Maximum permissible compressive stress shall be limited to 0.4 of the minimum works test cube crushing strength specified.

- Tensile stress shall be limited upto 5.3 N/Sq.mm due to working load moment/first crack moment and 3.0N/Sq.mm due to average permanent load moments respectively.

- Manufacture

  - Moulds

    - Moulds shall be of steel and  shall be of rigid construction to prevent distortion. The moulds shall not allow any leakage of cement grout in casting. The holes in the end plates, for the H.T. wires shall be accurately drilled by jig to ensure interchangeability.

    - In the case of the long line method of manufacture the casting bed shall have provision to ensure correct alignment of the moulds. The moulds shall be free to move/slide along the line to permit transfer of prestressing force along the line without restraint.

  - Stretching of wires

    - The prestressing wires shall be stretched by an approved method. In the stretching of the H.T.S. wires, the tensile stress in the wires shall not exceed 80% of the specified minimum ultimate tensile strength. The anchoring of the stretched wires shall be such that during manufacture and until the wires are released, no slipping occurs.

    - The tensioning of prestressing steel shall be carried out in a manner that will induce a smooth and even rate of increase of stress in the wires.

    - The force induced in the prestressing wires shall be determined by means of calibrated gauges only attached to the tensioning apparatus and cross-checked by extension of the wires observed. The extension to be achieved shall be determined in advance based on

    - trials conducted on representative samples of the wires used in the poles the force to be adopted for stretching each wire shall allow for the frictional resistance encountered in stretching.

  - Mixing and consolidation of concrete

    - Provision shall be made to measure the quantities of cement and of fine and coarse aggregates by weight only. The accuracy of the measuring equipment shall be 3%. All the measuring equipment shall be maintained in a clean, serviceable condition and its accuracy checked regularly. Volume batching shall not be permissible. Modern high speed mixer preferably pan or Turbine type, approved by the Engineer shall be used for mixing the concrete.

    - Mixing and placing of concrete shall as far as possible be avoided during the extreme temperature in summer and winter. The concreting shall commence within one hour of stressing of the wires. Failing which the High Tensile Steel wires shall be checked and re-tensioned if necessary.

    - The manufacture of poles shall be done under suitable cover and the poles shall not be cast in the open.

    - The concrete shall be thoroughly mixed and consolidated by means of high frequency vibrators. The extent of vibration required for obtaining full consolidation should be determined on actual field trials.

    - The freshly cast poles shall be protected during the first stage of hardening from the harmful effects of sunshine, dry winds, cold and rains.

  - De-tensioning of Wires :

    - The anchoring system shall provide a device for gradual de-tensioning of the wires. No back pulling of the wires shall be permitted in the gradual de-tensioning device for the purpose of release of any wedge or other parts of the de-tensioning device. Flame cuttings of the wires before release of the full tension shall be strictly prohibited.

    - The transfer of prestress shall not be effected until the concrete in the pole has attained the strength specified in Clause 4.1 (ii) above as established by control tests on cubes specified in Clause 6.3.1.

  - Curing

    - The curing of the concrete shall be by water curing till the strength for transfer prestress is attained. The curing of poles shall be carried out by covering the poles with empty gunny bags and constantly wetted prior to de-tensioning and after de-tensioning the poles are cured in the ponds for balance specified period. The poles during this period of curing shall not be allowed to dry out at any cost. In case the bidder resorts to steam curing, the curing cycle may be got approved by the Engineer.

  - Earthing

    - Earthing shall be provided by having a length of 8.00 SWG G1 wire embedded in concrete during manufacture and the ends of wire left projecting from the pole to a length of 100 mm at 250 mm from top and 150 mm below ground level.

    - The earth wire shall not be allowed coming into contact with pre-stressing wires.

5.7.	Supervision :

    - A competent and qualified person shall be employed by the manufacturer whose duty will b e to supervise at all stages of the placement of the concrete. All tests on materials the making and testing of cubes, the maintenance and calibration of all mixing and measuring plants and gauges shall be carried out under his direct supervision. He shall also maintain a direct record of the quantities, proportions and source of supply of aggregates used, nature and duration of curing actually done, the results of internal as well as external tests etc. these records shall be kept available for scrutiny by the Engineer at all times. The name of the competent person shall be intimated to the Engineer before commencing manufacture.

  - Tolerances :

    - The tolerance on overall length of the poles shall be + 15 mm. The tolerance on cross-sectional dimensions shall be +3mm. The tolerance on uprightness of the pole shall be 0.5 per cent.

  - Finish

    - All poles shall be free from surface defects including hair cracks. The surface of the poles in contact with the steel moulds shall be smooth and regular in shape, and as far as possible, be free from pores. Water retaining pockets or honey combing formations shall not be admissible.

    - The ends of the pre-stressing wires shall be cut as close to the surface of the poles as possible and in any case, shall not project more than 3 mm.

    - The ends of high tensile steel wires shall be given two coats of suitable epoxy or anticorrosive paints approved by the Engineer.

  - Stacking in Lots :

    - After the poles have been checked both dimensionally and from the point of view of finish they shall be stored at a convenient place in lots, each lot comprising of all pole cast together and de-tensioned simultaneously in one long line (of single or multiple moulds).

    - The poles shall be stacked on leveled and consolidated grounds, on one another upto a height corresponding to not more than 15 poles. Each pole shall be separated from the other vertically by wooden battens of size 50mmX50mm to ensure that the poles are stacked evenly without damages.

- Inspection and Testing

  - Inspection :

    - The Contractor shall supply at his expense all the poles required for tests and for retest, samples of materials and all labour, machines, tools, gauges, apparatus, forms of tests reports etc., and all things which may be necessary or required by the Engineer for carrying out any or all of the checks and tests mentioned in the specifications and shall tender all reasonable assistance in making such checks and tests.

One pole for every 200 poles shall invariably be tested to destruction.

    - All pressure gauges and measuring dials on the compression test machines, pre-tensioning equipment, static bending Test Machine, Weight Batching Machine shall be got checked and calibrated regularity as directed by the Engineer by an independent agency and the adjustment certificates shall be furnished to the Engineer. The frequency of calibration of different gauges is given below.

Frequency for calibration of different gauges and testing equipment

| 1 | Cube testing machine | Once in six months |
| --- | --- | --- |
| 2 | Weight | Every week or after casting 500 poles which ever is earlier |
| 3 | Pole testing machine | After testing 250 poles on machine jack or three months whichever is earlier. |
| 4 | Tensioning jack | Every three months or after tensioning 5000 poles whichever is earlier. |
| 5 | Dimensional gauges | Three months or after checking 5000 poles whichever is earliner |

    - The Engineer shall have free access at all times to the works in which the poles are manufactured. They shall be at liberty to inspect the manufacture at any stage and to reject any material or work, not conforming to the terms of this specifications.

  - Check and Tests :

    - In addition to the control checks exercised o the materials and manufacturing process specified in Clause 3 & 4 above, the concrete and finished pole shall be subject to the following periodical checks and tests.

1.	Compressive strength test of concrete at 20 days.

2.	Compressive strength test of concrete of deternsioning.

3.	Modulus of Rupture test of concrete

4.	Check for dimensional tolerances and surface finish of poles

5.	Statistic bearing strength test of poles.

    - For the purpose of testing and acceptance of poles each lot shall be as defined in Clause 5.9.1. above.

    - Pole to be tested shall be selected at random by the Engineer. One hour before the tests, the poles shall be given a coat of lime wash in order to make the cracks easily visible. The poles shall be tested as per the proforma vide Annexure II, III and IV.

  - Compressive Strength tests of concrete

    - Test cubes of size 15 cm X 15 cm X 15 cm shall be made and consolidated from the same concrete simultaneously with the poles. The cubes shall be cured along with the poles in the same manner and tested prior to transfer of prestress, to check that the concrete has developed the requisite minimum compressive strength specified at transfer. The remainder of cubes shall be cured as specified in IS-456-1964 and tested at the end of 28 days to determine the concrete strength at that age. The prestress will be released only if the concrete for as attained the minimum strength at transfer.

  - Modulus of rupture test of concrete

    - The modulus of rupture test of concrete shall be carried out on concrete poles as specified in IS-516. The results obtained shall be supplied to the Engineer for information.

  - Check for Dimensional Tolerance and finish

    - The poles shall be examined visually for finish and free from surface defects. The dimensional tolerances specified, directed by the Engineer.

  - Static Bending Strength test of poles

    - The following cracking failure moments of the poles shall be ascertained by recording the corresponding loads.

1.	First crack moment

2.	Failure moment

    - The cracking moment shall be that moment at which when a load is applied on the pole for testing as in Clause 6.6.4 below, the pole just begins to develop hair line crack(s) barely perceptible to the naked eye of a length of 15 mm and above. The failure moment shall be the moment corresponding to that load beyond which a further load increment shall be no longer possible due to the progressive deflection of pole.

    - The loading arrangements for conducting the static bending strength tests shall be with the load applied at 0.6 m from top of the pole. Bottom supports shall be carefully fixed to avoid un-even leveling and the bearing surfaces shall be proper to ensure uniform line contact with concrete surface. Any roughness and unevenness of concrete in the tearing area shall be made up with plaster of Paris gypsum or suitable rubber packing. The testing shall be done at point of application of load, fixing the pole from the bottom at 1.5m height.

    - When testing the concrete poles the formation of the hair cracks shall be carefully observed and the load shall be increased upto the point at which hair cracks just perceptible to the naked eye appear and load noted. The loads shall be increased at the rate of 50 Kgs the interval between two instalments being 1 minute for observing cracking moment and failure moment.

  - Frequency of check and testing :

    - For each lot of poles, compressive strength tests on concrete both at 28 days and transfer of load shall be carried out on a minimum of 3 cubes each time.

    - The modulus of rupture test of concrete shall be carried out at the rate of one pole per day for the first 1500 poles produced. Thereafter, it will be sufficient if a minimum of one pole is tested for week’s production.

    - For the check and tests on the poles, the number of poles to be tested and the frequency of testing shall be as follows :

      - (i) Dimensional checks and surface finish :

The frequency of dimensional check shall be at the rate of 10% from each lot of pole for dimensions like length, breadth, width where such dimensions depend up on the accuracy of the mould.

(ii) Static bending strength

In case of lots whose works concrete cube strength is equal to or more than                400 Kg/Sq.cm, the Static Bending tests as per Clause 6.6.3., shall be carried out at 0.6m from top of pole at the rate of one pole for every 200 poles manufactured.

    - Inspection

The APSPDCL may carry out inspection at any stage of manufacture. The successful tenderer shall grant free access to the purchaser’s representative at a reasonable time when the work is in progress. Inspection and acceptance of any material under this specification by the purchaser shall not relieve the Contractor of his obligation of furnishing materials in accordance with the specification and shall not prevent subsequent rejection if the material is found to be defective.

The Contractor shall keep the purchaser informed in advance about the manufacturing programme so that arrangements can be made for inspection. The purchaser reserves the right to insist for witnessing the acceptance/routine testing of the bought out items. The Contractor shall give 15 days (for local supply) 30 days (in case of foreign supply) advance intimation to enable the purchaser to depute his representative for witnessing the acceptance and routine tests.

- Acceptance of poles

  - The standard of acceptance for the cube test on concrete

The compressive strength shall be as specified in clause 4.1. and 4.2. where the compressive strength of concrete at 28 days as determined above, falls below 400 Kg/Sq.com, the corresponding lots of poles shall be rejected.

  - Dimensional tolerances and surface finish :

The checked poles shall comply with the dimensional tolerance and surface finish as specified in Clauses 5.8 and 5.9.

  - A lot of poles shall be considered acceptable, if compressive strength of the concrete is acceptable and the corresponding test pole from the lot passes all the tests mentioned in Clauses 6.2 to 6.6. above.

- Re-tests

  - If any of the poles tested for Static Bending Strength as per Clause 6.6.3 above fails to fulfil the values in Clauses 7.3., two additional poles from the same lot shall be selected for re-testing and if both those poles pass the test, the lot presented by these pole shall be accepted if the lot is otherwise acceptable except for the poles which originally failed in the test. If either of those two additional poles fail, the whole lot shall be rejected.

- Loading and desptaching

  - Only those poles which have been passed by the Engineer shall be loaded for dispatch.

- Guarantee

  - The Contractor shall guarantee the poles for a period of 18 months from the date of delivery or one year after they have been put in service in line, whichever is earlier. If during the guarantee period, any poles are found to develop defects attributable to bad materials and workmanship requiring withdrawal from service, the cost of replacement shall be borne by the Contractor. The defective poles withdrawn from service shall be handed over at site to the Contractor for his disposal. The Contractor shall make good the cost of replacement within 60 days of advice of defects, during which period, the Contractor or his representative shall be given permission to inspect the poles, make his observations and carry out check or examine jointly with the Engineer.

TECHNICAL SPECIFICATION

FOR ALL ALUMINIUM ALLOY CONDUCTOR (100 Sqmm, 55 Sqmm & 34 Sq.mm)

1. SCOPE :

  - This specification provides for the manufacture, testing before dispatch, supply and delivery of all Aluminium Alloy (Aluminium + magnesium + Silicon) Stranded conductors for overhead Power Transmission purposes.

2.	STANDARD :

The conductors shall comply in all respects with the latest versions of REC 33/84 R(1991) Specification and IS 398 (Part-IV) 1994 with at least amendments if any.

3.	CLIMATIC CONDITIONS :

i)	Peak ambient temperature in shade				50 deg. C

ii)	Maximum average ambient temperature			40 deg. C

over a 24 hours period in shade

iii)	Maximum temperature attainable by an 			70 deg. C

object exposed to sun

iv)	Minimum ambient temperature				7.5 deg. C

v)	Maximum relative humidity					100%

vi)	Average number of thunderstorm days per annum	50

vii)	Average number of dust storms				10

viii)	Average number of rainy days per annum			90

ix)	Average rainfall per annum					925 mm

x)	Number of months of tropical monsoon conditions 		4 months

xi)	Maximum wind pressure					260 Kg/Sq.mm

xii)	Altitude not exceeding					1000 Mtrs.

Above MSL.

4.  MATERIALS :

The materials offers shall be of best quality and workmanship. The conductors shall be constructed of heat treated Aluminium-Magnesium Silicon alloy wires containing approximately 0.5% magnesium and 0.5% Silicon and having the mechanical and electrical properties specified in appendix –I enclosed. the wires shall be smooth and free from all imperfections such as spills and splits. The surface of conductor shall be free from points, sharp edges, abrasions or other departures from smoothness or uniformity of surface contour that would increase radio interference and corona losses. When subject to tension upto 50% of the ultimate strength of the conductor. The surface shall not be depart from the cylindrical form nor any part of the component parts or standards relative to each other in such a way as to get out of place and disturb the longitudinal smoothness of the conductor.

5.	Size and Properties :

The size and properties of Aluminium Alloy Conductor shall be as given in the Appendix-I & II enclosed which also indicate the values of resistance and weights.

6.	Tolerance :

The following tolerance shall be permitted on nominal diameter.

Tolerance on nominal diameter 	Plus or Minus one percent (+/-1%)

Aluminium alloy Wires

7.	a) The Co-efficient of linear expansion per deg. C shall be 23.0X10-6 (E)

b) Final modulus of Elasticity (Practical) 0.6234 X 10-6 Kg/Sq.mm.

8.	Joint in Wires

No joints are permitted in seven standard conductors

- STRANDING:

  - The wires used in construction of a stranded all Aluminium Alloy conductor (AAAC) shall,  before stranding, satisfy all requirements of REC 33/84(R-1991) and IS 398 (Part –IV) 1994 with latest amendments thereof. The lay ratio shall be within the limits given under Col.10 below:-

  - The lay of the stranding shall be right handed. The wires shall be evenly and closely stranded.

- Lay ratio:

The lay ratio of different layers shall be within the limits given below:-

| No.of Wires in Conductors | 6 Wire layer |  |
| --- | --- | --- |
|  | Min | Max |
| 7 | 10 | 14 |

- packing and marking

  - The conductor shall be wound in non-returnable reels or drums conforming to IS 1778 of 1980 “Specification for reels and drums for bare conductor or the latest versions thereof. The drums shall be marked with the following :

- Manufacturer’s Name

- Trade Mark, if any.

- Drum number or Identification number

- Size of Conductor

- Number and lengths of piece of conductor in each drum (No/Meters)

- Gross mass of the packing(Kg)

- Net mass of Conductor (Kg)

- ISI Specification Mark, the purchase order number containing and identification mark and letter “APSPDCL”

  - The drums shall be of such construction as to ensure delivery of conductor in the field free from displacement and damage and shall withstand all stresses of handling and stringing, so that the conductor surface is not cut, dented, scratched or damaged in any way during manufacture, Transport & Stringing.  The conductor shall properly lagged on drums and shall be notched to suit the drum and held in place of Steel strapping. Method of lagging to the employed may be clearly stated in the tender.

  - The conductor drum should be suitable for wheel mounting, before reeling, the cardboard or other suitable material shall be secured to the drum and inside flanges of the drums. After reeling, the exposed surface area of conductor shall be nearly wrapped with suitable soft material to protect the conductor from dirt and grit.

  - The gross weight of each package shall not exceed the following limits, subject to a tolerance of +10%

100 Sq.mm Aluminium Alloy		area (7/4.26mm AAAC) 2000 Kg

55 Sq.mm Aluminium Alloy		area (7/3.15mm AAAC) 1500 Kg

34 Sq.mm Aluminium Alloy		area (7/2.50mm AAAC) 1100 Kg

  - The minimum standard length of following sizes of AAAC shall not be less than 2 KM. Much longer lengths are preferred. Short lengths (not less than 50% of the standard length shall be acceptable only to the maximum extent of 10% of the quantity ordered for each size).

100Sq.mm	Conductor	1.1KM

55Sq.mm	Conductor	1.7KM

34 Sq.mm       Conductor	2.0KM

- TESTS:

The following test shall be carried out on wires used for AAAC as per detailed procedures given in the IS 398 Part-IV/1994 with latest amendments thereof.

- Breaking Load Test

ii) 	Elongation test.

iii)	Resistance.

12.1.	The rejection and retest procedure shall be followed as stipulated in IS:398/Part-IV of 1994, or any other latest amendments thereof.

- Inspection:

All tests and inspections shall be made at the place of manufacturer unless otherwise specifically agreed upon by the purchaser. The manufacturers shall afford the Inspector representing the purchaser all reasonable facilities, without charge, to satisfy him that the material is being furnished in accordance with this specification.

The purchaser has the right to have the tests carried out at his own cost by an independent agency whenever in dispute regarding the quality of supply.

- checking and verification of length of conductors:

The Contractor /manufacturer of  conductor should arrange for the inspection by the representative of the purchaser specially authorized for this purpose. Atleast 10 % of the total number of drums of conductors taken at random should be checked to ascertain the length of conductor adopting the following method.

- The drum with the AAA Conductor shall be weighed, four or five empty reels normally used for winding the AAAC shall also be weighed. Net weight of the AAAC shall be calculated by subtracting average weight of the empty reel from the Gross weight of the drum containing AAAC.  Having known the weight of the AAA Conductor and other parameters of the conductor its length can be computed.

Alternatively

- Transfer the AAAC from one reel to the other while at the same time measuring the AAAC so transferred by means of a meter. Arrangements should be made available in the works of the manufacturer for transferring the conductor from one reel to another at the same time measuring the length of conductor so transferred by means of a meter.

- Guaranteed Technical Particulars:

The Bidder shall furnish the guaranteed technical particulars as per Appendix-III enclosed and submit the same with his tender.

# APPENDIX – I

Size and properties of Aluminum alloy wires used in the construction of stranded all aluminum alloy conductor

| Nominal Aluminium Area | Nominal Size mm | Min mm | Diameter Max. mm | Cross sectional area of Nominal diameter | Mass Kg/Km | Minimum braking load after stranding KN | Resistance at 20 deg.C Maximum | Standard Resista-nce |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| Sq.mm | Mm | Mm | Mm | Sq.mm | Kg/Km | KN | Ohm/KM | Ohm/KM |
| 100 | 4.26 | 4.22 | 4.30 | 14.25 | 38.48 | 4.18 | 2.345 | 2.280 |
| 55 | 3.15 | 3.12 | 3.18 | 7.793 | 21.04 | 2.29 | 4.290 | 4.170 |
| 34 | 2.5 | 2.47 | 2.53 | 4.909 | 13.25 | 1.44 | 6.845 | 6.620 |

APPENDIX – II

PROPERTIES OF ALUMINIUM ALLOY STRANDED CONDUCTOR

| Nominal aluminium area | Stranding and wire dia | Sectional area | Approximate over all dia | Approximate mass | Calculate max resistance 20 deg. C | Approximate calculated breaking load |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 |
| Sq.mm | Mm | Sq.mm | Mm | Kg/Km | Ohm/Km | KN |
| 100 | 7/4.26 | 99.77 | 12.78 | 272.86 | 0.3390 | 29.26 |
| 55 | 7/3.15 | 54.55 | 9.45 | 149.20 | 0.6210 | 16.03 |
| 34 | 7/2.50 | 34.36 | 7.5 | 94.0 | 0.90 | 10.11 |

A P P E N D I X  – III

## GUARANTEED TECHNICAL PARTICULARS

FOR ALL ALUNINIUM ALLOY CONDUCTORS

| 1. | Maker’s Name and Address a) Aluminium Alloy Rods b) Complete Alloy Strand | : |  |
| --- | --- | --- | --- |
| 2. | Stranding and diameter of Aluminium Alloy strand | : |  |
| 3. | Overall diameter of conductor in mm | : |  |
| 4. | Standard nominal Aluminium alloy area in Sq.mm | : |  |
| 5. | Calculated Aluninium alloy area in Sq.mm | : |  |
| 6. | Minimum ultimate tensile strength of Aluninium Alloy Wire Strand in Kg | : |  |
| 7. | Guaranteed ultimate tensile strength of conductor in Kg. | : |  |
| 8. | Minimum breaking load in Kg. For a) Aluminium Alloy strand b) Aluminium Alloy conductor | : |  |
| 9. | Maximum working tension of conductor | : |  |
| 10. | Weight in Kg per KM of Aluminium Alloy conductor | : |  |
| 11. | Resistance in Ohm per KM at 20 deg. C | : |  |
| 12. | a) Continuous maximum current rating of conductor in still air 45 deg. C ambient temperature (Amps) b) Temperature rise for the above current (deg. C) | : |  |
| 13. | Modulus of Elasticity of Aluminium Alloy Conductor Kg/Sq.mm | : |  |
| 14. | Co-efficient of linear expansion per degree centigrade for - Aluminium Alloy Strand - Alloy Conductor | : |  |
| 15. | Standard length of each piece in KM | : |  |
| 16. | Dimension of the rate in Cms | : |  |
| 17. | Gross weight of the reel including weight of the conductor Kg. | : |  |
| 18. | Standard according to which the conductor will be manufactured and tested | : |  |
| 19. | Other particulars | : |  |

TECHNICAL SPECIFICATION

FOR PANTHER ACSR CONDUCTOR

1.0	SCOPE

1.1	This specification covers manufacture, testing before dispatch, packing and supply of 37/3.0 mm PANTHER ACSR Conductor for use on 132KV Transmission Lines.

2.0	STANDARDS

2.1	The conductor shall comply in all respects with the latest edition of IS 398 Part-ii-1996 with latest amendments unless other-wise stipulated in this specification or any other standard which ensures equal or higher quality of material.

2.2	The materials used in the manufacture of the ACSR conductor shall conform to the following standards.

i)	IEC-209	:	Specification for Aluminium Conductor Steel

Reinforced for overhead power transmission.

ii)	BS-215	:	Aluminium conductor steel reinforced for overhead

power transmission.

iii)	IS-209	:	Specification for Zinc.

iv)	IS-2633	:	Galvenisation

v)	IS-1778	:	Packing reels and drums for bear conductors.

vi)	IS-4826	:	Galvanised coating on round  steel wires.

vii)	 IS-1521     :	  IS-2429, IS-4324, IS-6743, IS-18412, IS-5484 methods of

testing & other processes.

3.0	GENERAL TECHNICAL REQUIREMENTS

3.1	The General Technical Requirements are given in Appendices-I & II. The conductor shall confirm to these technical requirements.

3.1.1	The bidder shall furnish guaranteed technical particulars in Appendix-III.

  - Materials

Important technical particulars are given hereunder:

The material offered shall be of best quality and workmanship. The steel cored aluminum conductor strands shall consist of hard drawn aluminium wire manufactured form not less than 99.5% pure electrolytic aluminium rods of E.C. grade. The steel wire shall be from material produced either by the acid or basic open hearth process or by electric process. No steel wire drawn from Bessemer process shall be used. The steel wire shall not contain sulphar exceeding 0.045% and phosphorous 0.035%. The chemical compositions of the steel wire should be as specified in Appendix-II.

The steel wires shall be evenly and uniformly coated with electrolytic high grade, 99.95% purity zinc complying with the latest issue of IS-209 for zinc. The uniformity of zinc coating and the weight of coating shall be in accordance with Appendix-II and shall be tested and determined according to the latest IS-2633 or any authoritative standard.

The steel strands shall be hot dip galvanized and shall have minimum zinc coating of 250gm/sq.m (before stranding) of the uncoated wire surface. The zinc coating shall be smooth, continuous, and of uniform thickness, free from imperfections and shall withstand minimum three dips after stranding in standard preece test. The steel strands shall be performed and postformed in order to prevent spreading of strands in the event of cutting of composite core wire.

3.3	SIZES

3.3.1	The size of steel cored aluminium conductor the resistance and weight shall be 	accordance with the values given in Appendix-I.

3.4	TOLERANCES

3.4.1	The following tolerances shall be permitted on standard diameter and on the resistance of aluminium wires.

Tolerance on standard diameter of  +1% aluminium wires.

Tolerance on the standard resistance +0.3% when corrected to standard weight and temperature.

3.4.2	A tolerance of plus or minus 2 (Two) percent shall be permitted on the standard diameter of the galvanized steel wire. The variation from the weights shall not be more than plus or minus (Five) percent.

3.4.3	The cross-section of any wire shall not depart from cincurity by more than an amount corresponding to the tolerance the standard diameter.

3.5	MODULUS OF ELASTICITY AND COEFFICIENT OF LINEAR EXPANSION

3.5.1	The value of the final modulus of elasticity for steel cored aluminium conductor is the average of values obtained for actual stress strain tests.

3.5.2	The coefficient of linear expansion for steel cored aluminium conductor has been calculated on the basis of coefficient linear expansion of 23.0 X 10-6 per degree centigrade of 		drawn aluminium and 11.3 X 10-6 per degree centigrade galvanized steel wires and represent only the even values. These values shall however be given by the bidder under the guaranteed  technical particulars.

3.6	SURFACE CONDITIONS

    - All aluminium and steel strands shall be smooth and free from all imperfections, spills, and splits. The finished conductor shall be smooth, compact, uniform and free from any imperfections including spills and splits. Die mark scratches, abrasions, scuff marks, kinks (protrusion of wires) dents, pressmarks, cut marks, wire cross-over, overriding, looseness, pressure and/or unusual bangle noise on tapping material inclusions, whits rust, powder formation on black spots ( on account of reacting with trapped rain water etc. Dirt, grit, etc. The surface of the conductor shall be free from points, sharp edges, abrassions or other departure from smoothness or uniformity of surface contour that would increase radio interference and corona losses. When subject tension upto  50% ot the ultimate strength of the conductor, the surface shall not depart from the cylindrical form of any part of the comonenet  parts on strands move relative each other in such a way as to get out of place and distance the longitudinal smoothness of the conductor.

  - JOINTS IN WIRES AND CONDUCTORS:

3.7.1	Aluminium wires

No joint shall be permitted in the aluminium wires in the outermost layer of the ACSR conductor. Joints in the individual aluminium wires in the layers are permitted. In addition to those made in the base rod or wire before firm drawing, but no two such joints shall be less than 15 m apart in the complete stranded conductor. The cold pressure butt-welding shall make such joint.

3.7.2	Galvanized steel wires

There shall be no joints except those in the base rod on wires before final drawing, in steel wires forming the core of the steel reinforced aluminum conductor.

  - STRANDING

    - The wires used in Construction of the standard conductor shall, before stranding, satisfy all requirements of IS-398 and as per Appendices-I & II.

    - In all Constructions the successive layers shall be stranded in opposite directions. The wires in each layer shall be evenly and closely stranded round the underlying wire or wires. The outermost layer of wires shall have a right hand lay. The lay ratio of the different layers shall be within the limits given under Appendix-I.

3.9	PACKING AND MARKING

    - The conductor shall be wound in non-returnable reels or drums conforming to IS:1778-1980 “Specification for Reels and Drums for bare wire” or any other authoritive standard and marked with the following:

- Trade name if any

- Name of the manufacturer

- Size of conductor.

- Length of conductor and

- Net weight of conductor

The bidders should submit their proposed drum drawings along with the bid.

3.9.2	The reels shall be of such Constructions has to assure delivery of conductor in the field free form displacement and damage and should be able to withstand all stresses due to handling and the stringing operations so that conductor surface is not ented, scratched or damaged in any way during manufacture, transport and erection. The conductor shall be properly lagged on the drums and the method of lagging to be employed may be clearly stated in the tender. It should be notched to suit the reel and held in place by steel strapping. Lagging shall bot be nailed or bolted in place.

    - The conductor drum should be suitable for wheel mounting. All wooden components shall be manufactured out of seasoned soft wood free from defects that may materially weaken the component part of drums. Preservative treatment for anti-termite/ anti-fungus small be applied to the entire drum conductor. The inner check of the flanges and drum barrel surface shall be painted with a bitumen based paint. Before reeling cardboard or other suitable weather proof material shall be secured to the drum and inside flages of the drum. Medium grade neft paper shall be used in between the layers of the conductor. After reeling the conductor the exposed surface should be wrapped with suitable soft material to prevent the conductor from getting contaminated with dirt and gret.  Any space between the drum lagging and conductor should be suitably filled with soft filler material compactly packed.

  - LENGTHS

    - The conductor shall be supplied in standard lengths of 1300 meters. A tolerance of plus or minus 5% on the standard length shall be treated at lengths. Not less than 95% of total quantity of the conductor shall be supplied in standard lengths. Thus the quantity of conductor in lengths shorter than standard ones shall not exceed 5% of the total quantity to be supplied. Further no single conductor length in respect of such 5% (Max) supply in random lengths shall be shorter than 70% of the standard length. Only one standard length or random length of conductor shall be wound on each drum.

4.0	TESTING

4.1	SELECTION OF TEST SAMPLES

4.1.1	Before dispatch from the works individual wire and finished steel core aluminium conductor shall be subjected to the tests as specified in the IS 398 or any other authoritative standard.

4.1.2	Sample for individual wires for test shall be taken before stranding from not less than 10% of the spoors in the case of aluminium wire and 10% of the wire coils in stranding, they shall be obtained by cutting 1.2 Mts from the outer end of the finished conductor from not more than 10%  of the finished reels.

4.1.3	The mechanical test shall be carried out on single wire only.

4.2	TESTS

4.2.1	All the type routine and acceptance tests required shall be carried out on the conductors as per detailed procedures given in latest edition of IS-398 (Part-II) – 1996 and IS-398 (Part-V).

4.3	CHECKING AND VERIFICATION OF LENGTH OF CONDUCTORS

4.3.1	The contractor should arrange for inspection by the representative of the purchaser specially authorised for this purpose. At least 5% of the total No. of drums of conductor (with a minimum of one drum during testing) taken at random should be checked to ascertain the length of conductor so transferred by means of a meter.

Arrangements should be made available at the works of the manufacturer for transferring the conductor from one reel to another at the same time measuring the length of the conductor so transferred by means of a meter.

APPENDIX-I

DETAILS FOR POWER CONDUCTOR OF ‘PANTHER’ ACSR

| S.No. | Particulars | Panther ACSR |
| --- | --- | --- |
| 1 | Conductor | ‘Panther’ steel cored Aluminium stranded conductor. |
| a | Stranding and core diameter Aluminium Steel | 30/3.00mm 7/3.00mm |
| b | Calculated equivalent area of aluminium | 207mm |
| c | Approximate total weight | 976Kg/ KM |
| d | Calculated resistance of conductor at 200 C | 0.140 Ohm/ Km |
| e | Ultimate strength of conductor. | 9127 Kg. |
| 2. i) | Minimum breaking load of steel wire. Before standing After stranding | 947 Kg. 900 Kg. |
| ii) | Minimum breaking load of Aluminium wire Before stranding After stranding | 119 Kg. 113 Kg. |
| 3 | Lay ratios Steel core Maximum Minimum Aluminium Layers 12 wire layer Maximum Minimum 18 wire layer Maximum Minimum | 28 13 16 10 14 10 |
| 4 | Final modulus of Elasticity | 0.787 X 10+4 Kg/ Sq.mm |
| 5 | Coefficient of linear Expansion | 17.73 X 10-6 per deg. C. |

APPENDIX – II

Solid steel and aluminium wires used in steel cored aluminium conductors

| S.No. | Particulars | Steel | Aluminium |
| --- | --- | --- | --- |
| 1. | Diameter of strand Maximum Minimum | 3.00mm 3.06mm 2.94mm | 3.00mm 3.03mm 2.97mm |
| 2 | Cross sectional area | 7.069 Sq.mm | 7.069 Sq.mm |
| 3 | Weight | 55.13 Kg/ KM | 19.11 Kg/ KM |
| 4 | Minimum ultimate tensile strength | 134 Kg/ Sq.mm | 16.83 Kg/ Sq.mm |
| 5 | Minimum breaking load Before stranding After stranding | 947 Kg 900 Kg | 119 Kg 113 Kg |
| 6 | Zinc coating No. and duration of dipping Minimum weight of coating | 240 Gms/ Sq.Mtr |  |
| 7 | Resistance of aluminium strand at 20 deg. C. Standard Maximum | 4.025 Ohm/ KM 4.065 Ohm/ KM |  |

TECHNICAL SPECIFICATION

FOR INSULATORS

1.	SCOPE:

This specification covers design, manufacture, testing at manufacturer’s works before despatch, supply and delivery of porcelain insulators.

2.	APPLICABLE STANDARDS:

2.1	The materials shall comply in all respects with the relevant Indian Standard Specifications with latest amendments indicated below or with relevant IEC publications or any other authoritative standards.  The materials shall be suitable for use on three phase 50 c/s power system.

a)  ISS 731 – 1976		Disc insulators

b)  ISS 3188 – 1965		Pin insulators

2.2	Material confirming to any other internationally accepted standard which ensures equal or higher quality than the standards indicated above will also be acceptable. Where the material offered is according to any such international standard, an English Version of the specification shall be attached to the tender.

3.	CLIMATIC CONDITIONS

3.1	i.  Max. Temperature of air in shade			:	50 Deg.C

ii.  Min. Temperature of air in shade			: 	7.5 Deg.C

iii.  Max. Temperature of air in Sun			:	70 Deg.C

iv.  Max. humidity					:	100%

v.   Average no. of thunder storms day per annum 	:	50

vi.   Average no. of dust storms per annum 		:	10

vii.   Max. rainfall per annum				:	3000 mm

viii.   Average rainfall per annum 			:	925 mm

ix.   Limits of ambient temperature

over period of 24 hours				:	47 Deg.C and	  	   								27 Deg.C in              									summer and 30&

7.5 Deg.C in

winter.

x.  Max. wind pressure					:	260Kg/Sq.Mtrs.

xi.  Altitude not exceeding				:         1000M above MSL

The materials offered shall be suitable for operation in tropical climate in which they will be subject to the full rays of the sun and inclement weather and should be able to withstand wide range of temperature variations. The humidity may be as high as 100% during rainy season and as low as 10% during dry season. The prevailing weather conditions are given above.

# 33KV & 11KV INSULATORS

All materials used in the manufacture of the disc insulators shall be of the best quality.

Unless otherwise specified, the glaze shall be brown in colour. The glaze shall be brown in colour. The glaze shall cover all porcelain parts of the disc insulator except those areas which serve as supports during firing or are left unglazed for the purpose of assembly.

Cement used in the construction of disc insulators shall not cause fracture by expansion or loosening by contraction and proper care shall be taken to locate the individual parts correctly during cementing.  The cement shall not give rise to chemical reaction with metal fittings and its thickness shall be as uniform as possible.

All fitting shall be designed so that the harmful bimetallic corrosion is avoided and effects of vibration both on conductors and fittings itself are minimized.  All ferrous parts exposed to atmosphere in service except those made of stainless steel shall be protected by hot dip galvanizing.  All castings shall be free from blow holes and other casting defects such as cracks etc.

The socket portion and shank pin of the disc insulator shall be made of high quality steel duly forged.

The “W” clips shall be made of good quality phosphor bronze or stainless steel, or copper alloy to give proper spring action and to provide locking arrangement.

## DESIGN AND TYPE

Type “B” insulators shall be offered.  Type “B” insulator is one in which the length of the shortest puncture path through solid insulating material is less than half the length of the shortest flashover path through air outside the insulator.

The technical particulars of the disc insulators required and the system requirements are indicted in Appendix.  The design of insulators shall be such that stresses due to expansion and contraction in any part of the insulator shall not lead to deterioration.

The disc insulators shall be ball and socket type in respect of 70 KN and        45 KN and also C&T type 45 KN.  The ball and socket of the disc insulator shall be heavily galvanized and mechanically strong.  The ball shall move free in the sockets, but shall be so designed that they do not give way while in service.

The sockets shall be made of copper bearing drop forged steel.  These shall be free from cracks, shinks air holes, burs and rough edges.  The socket shall be circular, with inner and outer surfaces concentric and of such design that they will not yield or distort under the stress to the porcelain shells.

The ball pin shall be a single piece made of drop forged steel and shall be free from laps, folds, burs and rough edges.  All bearing surfaces shall be smooth and uniform so as to distribute the loading stresses uniformly.  The ball pins shall be of such a design that they will not yield or distort under loaded condition.  The pins shall not be made by joining, welding, shrink fitting or any other process from more than one piece of material.

Security clips for use with ball and socket coupling shall be made of suitable material of stainless steel or copper alloy or phosporbronze.  The security clips shall provide positive locking of the coupling.  The logs of the security clips shall be spread after installation to prevent withdrawal from the socket.  C & T type disc insulators shall comply in all respect with the relevant IS.

4.5.	PORCELAIN

The porcelain used in the manufacture shall be sound, free from defects, thoroughly vitrified and smoothly glazed.  The porcelain shall not engage directly with the hardware.

4.6.	GLAZE

The finished porcelain shall be glazed in brown colour.  The glaze shall cover all exposed porcelain parts of the insulators, shall have a good luster, smooth surface and a good performance even under extreme weather conditions of tropical climate.  It shall not get cracked or chipped by ageing under normal service conditions.  The glaze shall have coefficient of expansion as that of the porcelain body throughout the working temperature range.

## WORKMANSHIP

The insulators covered by this specification shall be of latest design and conform to the latest scientific methods and shall be suitable for use on 11 KV 33 KV & 132 KV lines.  Sound design, latest manufacturing processes and proper material quality control shall be ensured at various stages.  Good finish and elimination of sharp edges and corners shall also be ensured.  The disc insulator shall be free from all sorts of defects.  All exposed surfaces shall be smooth and free from imperfection.

The forged metal sockets and shank pins shall be free form cracks, seams, shrinks, air-holes and rough edges.  Metal pins shall be free from laps, folds, seams bars and rough edges.  All surfaces of metal parts shall be perfectly smooth with no projecting points or irregularities.

All the ferrous parts shall be hot dip galvanized in accordance with the latest edition of IS.  The zinc coating shall be adherent, smooth, reasonably bright, continuous and free from such imperfections such as flux, ash, rust staines, bulky white deposits and blisters.  Bituminous paint coating shall be provided on the metal portion in contact with the cementing.  The insulator units after assembly shall be concentric and co-axial within the limits as permitted by the relevant Indian Standards.

5.	11 KV AND 33 KV PIN INSULATORS

General Requirements:

The porcelain shall be sound, free from defects, thoroughly vitrified and smoothly glazed.

Unless otherwise specified, the glaze shall be brown in colour.  The glaze shall cover all the porcelain parts of the insulators except those areas which serve as supporters during firing or are left unglazed for the purpose of assembly.

The design of the insulator shall be such that stresses due to expansion contraction in any part of the insulator shall not lead to deterioration.  The porcelain shall not engage directly with hard metal.

Cement used in the construction of the insulator shall not cause fracture by expansion or lessening by contraction and proper care shall be taken to locate the individual parts correctly during cementing.  The cement shall not give rise to chemical reaction with metal fittings and its thickness shall be as uniform as possible.

  - TYPE OF INSULATORS

Over head line insulators shall be of Type “B” as defined in Indian Standards. Type “B” Insulators or Insulator unit is the one in which the length of the shortest puncture path through solid insulating material is less than half the length of the shortest flashover path through air outside the insulator.

INSULATOR CHARACTERISTICS

The insulators shall have the electrical and mechanical characteristics which are given in the table given below:

ELECTRICAL:

The test voltage of insulators shall be as under:

| Highest System Voltage | Wet Power frequency withstand test | Power frequency puncture withstand test | Impulse Voltage withstand test |
| --- | --- | --- | --- |
| KV (RMS) | KV (RMS) | KV (RMS) | KV (PEAK) |
| 12 | 35 | 105 | 75 |
| 36 | 75 | 180 | 170 |

In this standard, power frequency voltages are expressed as peak values divided by \ /2 and impulse voltages are expressed as peak values.

The withstand and flash over voltages are referred to the reference atmospheric conditions.

The minimum failing load of insulators shall be 5 KN.

CREEPAGE DISTANCE:

The minimum creep age distance shall be as under :

| Highest system Voltage | Normally polluted atmospher |
| --- | --- |
| KV | Mm |
| 12 | 230 |
| 36 | 580 |

6.	TESTS

  - TYPE TESTS  :

All type tests shall be conducted as per the relevant Indian Standard specifications and a copy of the test certificate shall be furnished invariably along with the tender.

6.2.	ACCEPTANCE AND ROUTINE TESTS  :

All routine tests shall be conducted as per the relevant Indian Standard specifications in the presence of purchasers representative.

6.3.	MARKING  :

Marking on the materials shall be done as per the relevant Indian Standard Specification.

7.0.	INSPECTION  :

All acceptance tests and inspection shall be made at the place of contractor unless otherwise especially agreed upon by the contractor and purchaser at the time of purchase.  The contractor shall afford the inspector representing the purchaser all reasonable facilities without charge, to satisfy him that the material is being furnished in accordance with this specification.  The purchaser has the right to have the tests carried out at his own cost by an independent agency wherever there is a dispute regarding the quality of supply.

8.	PACKING  :

The packing shall be done as per the manufacturer standard practice.  However, he should ensure the packing is such that, the material should not get damaged during transit by Rail/Road.

9.	GUARANTEED TECHNICAL PARTICULARS  :

The guaranteed technical particulars shall be given as per Appendix.  Dimensional drawings shall be furnished wherever necessary.

APPENDIX

GUARANTEED TECHNICAL PARTICULARS FOR 33KV & 11KV DISC INSULATORS:

| Sl.No | Characteristic | 33KV | 11KV (B&S) | 11KV (C&T) |
| --- | --- | --- | --- | --- |
| 1. | Type/description |  |  |  |
| 2. | Colour and surface porcelain portion |  |  |  |
| 3. | Ferrous parts |  |  |  |
| 4. | Check chip provided in socket |  |  |  |
| 5. | Ball pin |  |  |  |
| 6. | Socket fitting |  |  |  |
| 7. | Mechanical & Electrical strength |  |  |  |
| 8. | Ball pin designation |  |  |  |
| 9. | Diameter and spacing of dia the insulator spacing |  |  |  |
| 10. | Min. failing loan of the insulator |  |  |  |
| 11. | Min. creep age distance |  |  |  |
| 12. | Min. protected creep age distance |  |  |  |
| 13. | One minute power frequency withstand voltage :Dry |  |  |  |
| 14. | One minute power frequency withstand voltage : Wet |  |  |  |
| 15. | Visible discharge voltage (Power frequency voltage) |  |  |  |
| 16. | Power frequency puncture voltage |  |  |  |
| 17. | Impulse flashover voltage Positive Negative |  |  |  |
| 18. | Flashover power frequency voltage : Dry |  |  |  |
| 19. | Flashover power frequency voltage : Wet |  |  |  |
| 20. | Standards according to which the porcelain insulators shall be manufactured and tested |  |  |  |
| 21. | No. of units for suspension / tension strings |  |  |  |

GUARANTEED TECHNICAL PARTICULARS FOR 11KV & 33KV PIN INSULATORS

1.  Marker’s Name & Country					    11KV          33KV

2.   i) Rating of pin insulators

ii) Electrical characteristics of insulators

a) Normal system voltage				KV

b) Highest system voltage				KV

c) Visible discharge test voltage

(Power frequency)				KV (RMS)

d) Dry one minute withstand voltage		KV (RMS)

e) Wet power frequency withstand voltage	KV (RMS)

f) Power frequency puncture withstand voltage	KV (RMS)

g) Impulse withstand voltage

(1/50 Micro second wave)			KV (PEAK)

h) Impulse flashover voltage

(1/50 Micro second positive voltage)		KV (PEAK)

i) Impulse flashover voltage

(1/50 Micro second negative voltage)		KV (PEAK)

j) Dry flashover voltage				KV

k) Wet flashover voltage				KV

3.     Mechanical characteristics of insulators :

a) Min. failing load				KN

b) Min. creep age distance			mm

4.     Colour of glaze

5.    Weight per unit

6.    Size of insulator

7.    Material of thimble

8.    Whether pin insulator is suitable for

use with small steel head/large steel head

9.     Standard to which the insulator shall be

manufactured and tested.

10.    Contents of each package and packed weight

11.    Tolerance in dimensions, if any

12.	Other Particulars if any

TECHNICAL SPECIFICATION

FOR AB SWITCHES

(33KV 800A, 11KV 400A & 11KV 200A)

1. SCOPE :

The specification provides for the manufacture, testing before dispatch, packing forwarding supply and delivery at destination stores (FADS) of 1) 33KV 800 Amps AB Switch metallics  2) 11KV 400A conventional AB Switches with insulators  3) 11KV 200A conventional type AB switch metallics.

2. STANDARDS :

A) 33KV 800 A AB Switch metallics : The 33KV, 800AAB Switches shall confirm in all respects to Tender Spn No. SPMPT – 22/02-03 IS:9920 part I to IV (latest version) and IS – 9921 part I – IV (latest version)

B) 11KV, 400A conventional AB Switches with solid core insulators :  The 11KV 400A AB Switches shall confirm in all respects to tender spn No. SPMPT – 22/02-03, IS 1818/1972, IS – 9920 part I to IV (latest version), IS : 9921 part I to IV (latest version).

C) 11KV, 200A conventional AB Switch metallics :  The 11KV 200A conventional AB Switch metallics shall confirm in all respects to tender spn No. SPMPT – 22/02-03, IS 1818/1972, IS – 9920 part I to IV (latest version).

3) DIMENSIONS : The dimensions of 1) 33KV 800A AB Switch metallics 2) 11KV, 400A conventional type AB Switch metallics 3) 11KV, 200A conventional type AB switch metallics and 4) 11KV, 400A solid core insulators shall confirm in all respects to IS as mentioned above.

4) DRAWINGS : The successful tendereres before proceeding for manufacture of the material, the detailed drawing shall be got approved by this office. The tenderers also required to produce three sets of drawings together with bill  of materials along with the tender.

5) TESTS AND TESTS CERTIFICATES :

i) As soon as the material is get ready for desptach, the material is to be offered for inspection by Registered Post and the tests as per the standards are to be carried out in the presence of APSPDCL representative without any cost and test certificates shall be got approved by this office.

ii) Latest type test certificates conducted at any standard organization are to be enclosed along with the tender. The tenders received without type test certificates are liable for rejection.

iii) The SPDCL reserves the right to carryout the tests by any standard organization at your cost, in case of any discrepancy regarding the quality of materials.

6) GUARANTTED TECHNICAL PARTICULARS :  The Guaranteed Technical Particulars as per the IS shall be guaranteed and statement of Guaranteed Technical particulars shall be furnished along with the tender.

7) NAME PLATE :  Equipment should be provided with name plate giving full details of manufacture, capacities and other details as specified in the relevant ISS or other specification stipulated. The Purchase  Order No. and date and year of supply and words APSPDCL must be etched on the name plate.

8. ASSEMBLY : The Assembly of the AB Switches at the destination stores is the responsibility of the Contractors.

- For 33 KV 800A AB Switches:

1. Operating down pipe  		: 6.1 Mts, 32 NB Class-B GI Pipe

2. Connectors (Jumper plate) 		: LM –6 Alloy terminal connectors (75X12

mm) suitable for panther conductor.

3. Fixed Contact			: 25X4 mm Copper Flat ( HDE)

4. Moving Contact			: 38 OD and 30 ID Copper Pipe ( HDE )

5. Base Channel			: 100X50 mm MS Channel of length 1065 mm

6. Provision for pad lacking in ON-OFF position shall be provided.

7. Three numbers Guides of MS Angle 50X50X6 mm for supporting the down

pipe, slotted holes are to be mate to the angles for fixing the same to the pole.

- For 11 KV 400A Conventional AB Switches:

1. Operating down pipe  		: 6.1 Mts, 32 NB Class-B GI Pipe

2. Terminal Connectors			: LM –6 Alloy terminal connectors Suitable for

Dog ACSR conductor.

3. Fixed Contact			: 25X4 mm Copper Flat ( HDE)

4. Moving Contact			: 32X6.5 mm HDEC Flat

5. Flexible Jumper			: Two numbers flexible jumpers of size

25X4X360 mm

6. Base Channel			: 75X40 mm MS Channel of length 609.6 mm

7. Provision for pad lacking in ON-OFF position shall be provided.

8. Three numbers Guides of MS Angle 40X40X5 mm for supporting the down

pipe, slotted holes are to be mate to the angles for fixing the same to the pole.

- For 11 KV 200A Conventional AB Switches:

1. Operating down pipe  		: 6.1 Mts, 32 NB Class-B GI Pipe

2. Terminal Connectors	: LM –6 Alloy terminal connectors Suitable for 20/30/50 ACSR conductor.

3. Fixed Contact			: 25X4 mm Copper Flat ( HDE)

4. Moving Contact			: 32X5 mm HDEC Flat

5. Flexible Jumper			: Flexible jumpers of size    25X4X360 mm

6. Base Channel			: 75X40 mm MS Channel of length 609.6 mm

7. Provision for pad lacking in ON-OFF position shall be provided.

8. Three numbers Guides of MS Angle 40X40X5 mm for supporting the down

pipe, slotted holes are to be mate to the angles for fixing the same to the pole.

GUARANTEED TECHNICAL PARTICULARS

FOR 33KV 800A AB SWITCHES

| S. No. | Details | 33KV 800A |
| --- | --- | --- |
| 1. | Whether single break or double break |  |
| 2 | No. of poles |  |
| 3. | Frequency |  |
| 4. | Voltage rating |  |
| 5. | Current rating in Amps |  |
|  | i) Normal |  |
|  | ii) Maximum with duration |  |
| 6. | Temperature rise of the following at full rated current in Degree over ambient temperature |  |
|  | i) Copper contract with coating |  |
|  | ii) Terminals of switches intended to be bolted to the external conductor |  |
|  | iii) Metallic parts acting as springs |  |
| 7 | Whether contacts are silver coated or tin coated |  |
| 8. | Volt drop across terminals of poles |  |
| 9. | Short time current and duration |  |
| 10. | Material of fixed contract & size |  |
| 12. | Material of moving blade & size |  |
| 13. | Material of terminal connector |  |
| 14. | Type diameter and length of operating pipe |  |
| 15. | Material of arcing horns |  |
| 16. | Size & Length of base mounting channel (Hot dip Galvanised) |  |
| 17. | Whether dimensional drawing is enclosed with the tender |  |
| 18. | Whether the air break switch is complete with all accessories |  |
| 19. | Minimum clearance between phases (The center distance between the insulators of adjacent phases in the assembled position of switch) |  |
| 20. | Center to center distance between insulators of the consecutive poles of the same phase in the assembled position of switch (in mm) |  |
| 21. | Whether mechanical interlock has been provided for arcing swatches |  |
| 22. | Types of bearing used in |  |
|  | i) Rotating insulators stack |  |
|  | ii) Operating shaft |  |
| 23. | Impulse withstand voltage (peak) with 1/50 MS wave positive and negative polarity |  |
|  | i) Across isolating distance |  |
|  | ii) To earth between poles |  |
| 24. | One minute power frequency withstand voltage (RMS) across isolating distance to earth and between poles |  |
|  | i) Across isolating distance |  |
|  | ii) To earth between poles |  |

Signature of the Tenderer

GUARANTEED TECHNICAL PARTICULARS

FOR 11KV 400A   CONVENTIONAL TYPE AB SWITCHES

| Sl. No. | Details | 11KV 400A |
| --- | --- | --- |
| 1. | Whether single break or double break |  |
| 2 | No. of poles |  |
| 3. | Frequency |  |
| 4. | Voltage rating |  |
| 5. | Current rating in Amps |  |
|  | i) Normal |  |
|  | ii) Maximum with duration |  |
| 6. | Temperature rise of the following at full rated current in Degree over ambient temperature |  |
|  | i) Copper contract with coating |  |
|  | ii) Terminals of switches intended to be bolted to the external conductor |  |
|  | iii) Metallic parts acting as springs |  |
| 7 | Whether contacts are silver coated or tin coated |  |
| 8. | Volt drop across terminals of poles |  |
| 9. | Short time current and duration |  |
| 10. | Material of fixed contract & size |  |
| 12. | Material of moving blade & size |  |
| 13. | Material of terminal connector |  |
| 14. | Type diameter and length of operating pipe |  |
| 15. | Material of arcing horns |  |
| 16. | Size & Length of base mounting channel (Hot dip Galvanised) |  |
| 17. | Whether dimensional drawing is enclosed with the tender |  |
| 18. | Whether the air break switch is complete with all accessories |  |
| 19. | Minimum clearance between phases (The center distance between the insulators of adjacent phases in the assembled position of switch) |  |
| 20. | Center to center distance between insulators of the consecutive poles of the same phase in the assembled position of switch (in mm) |  |
| 21. | Whether mechanical interlock has been provided for arcing swatches |  |
| 22. | Types of bearing used in |  |
|  | i) Rotating insulators stack |  |
|  | ii) Operating shaft |  |
| 23. | Impulse withstand voltage (peak) with 1/50 MS wave positive and negative polarity |  |
|  | i) Across isolating distance |  |
|  | ii) To earth between poles |  |
| 24. | One minute power frequency withstand voltage (RMS) across isolating distance to earth and between poles |  |
|  | i) Across isolating distance |  |
|  | ii) To earth between poles |  |
| 25. | PARTICULARS FOR INSULATORS |  |
|  | i) Type of insulators |  |
|  | ii) Name of manufacturer of insulators |  |
|  | iii) Height of the insulators |  |
|  | iv) Diameter of the largest shall |  |
|  | v) No. of units per stack |  |
| 26. | Electrical characteristics (For one insulator) |  |
|  | A) Flash over voltage |  |
|  | i) Dry Power frequency (KV) |  |
|  | ii) Wet power frequency (KV) |  |
|  | iii) Impulse voltage of 1/50 micro seconds (+Ve) (KVP) iv) Impulse voltage of 1/50 micro seconds (- Ve) (KVP) |  |
|  | B) Withstand Voltage |  |
|  | i) Dry Power frequency (KV) |  |
|  | ii) Wet power frequency (KV) |  |
|  | iii) Impulse voltage of 1/50 micro seconds (+Ve) (KVP) iv). Impulse voltage of 1/50 micro seconds (-Ve) (KVP) |  |
| 27. | Power frequency puncture withstand voltage of unit |  |
| 28. | Mechanical characteristics |  |
|  | i) Cantilever strength upright |  |
|  | ii) Cantilever strength under hang |  |
|  | iii) Torsinal strength (kgfm) |  |
|  | iv) Tensile strength |  |
| 29. | General characteristics |  |
|  | i) Minimum creepage distance mm |  |
|  | ii) weight of complete unit (Kg) |  |
| 30. | Standard to which insulator conforms |  |

Signature of the Tenderer

GUARANTEED TECHNICAL PARTICULARS

FOR 11KV 200A  CONVENTIONAL TYPE AB SWITCHES

| S. No. | Details | 11KV 200A |
| --- | --- | --- |
| 1. | Whether single break or double break |  |
| 2 | No. of poles |  |
| 3. | Frequency |  |
| 4. | Voltage rating |  |
| 5. | Current rating in Amps |  |
|  | i) Normal |  |
|  | ii) Maximum with duration |  |
| 6. | Temperature rise of the following at full rated current in Degree over ambient temperature |  |
|  | i) Copper contract with coating |  |
|  | ii) Terminals of switches intended to be bolted to the external conductor |  |
|  | iii) Metallic parts acting as springs |  |
| 7 | Whether contacts are silver coated or tin coated |  |
| 8. | Volt drop across terminals of poles |  |
| 9. | Short time current and duration |  |
| 10. | Material of fixed contract & size |  |
| 12. | Material of moving blade & size |  |
| 13. | Material of terminal connector |  |
| 14. | Type diameter and length of operating pipe |  |
| 15. | Material of arcing horns |  |
| 16. | Size & Length of base mounting channel (Hot dip Galvanised) |  |
| 17. | Whether dimensional drawing is enclosed with the tender |  |
| 18. | Whether the air break switch is complete with all accessories |  |
| 19. | Minimum clearance between phases (The center distance between the insulators of adjacent phases in the assembled position of switch) |  |
| 20. | Center to center distance between insulators of the consecutive poles of the same phase in the assembled position of switch (in mm) |  |
| 21. | Whether mechanical interlock has been provided for arcing swatches |  |
| 22. | Types of bearing used in |  |
|  | i) Rotating insulators stack |  |
|  | ii) Operating shaft |  |
| 23. | Impulse withstand voltage (peak) with 1/50 MS wave positive and negative polarity |  |
|  | i) Across isolating distance |  |
|  | ii) To earth between poles |  |
| 24. | One minute power frequency withstand voltage (RMS) across isolating distance to earth and between poles |  |
|  | i) Across isolating distance |  |
|  | ii) To earth between poles |  |

Signature of the Tenderer

(SPECIFICATION FOR 33 KV & 11 KV LINES)

1.  SCOPE: ERECTION OF 33 KV LINES ON 9.1 Mt. PSCC POLES.

The scope covers the survey of the proposed route, tree clearance where-ever necessary transport of material to the locations, erection of the line, testing of the line and handing over to the APSPDCL as per specification.  Materials such ass steel, cement, PSCC poles, top, cleats, clamps, washers, earth-wires.  H.B.G. metal, sand, water cost of bolts and nuts etc.  as given in Annexure-1 (B) are to be procured by the contractor cost of which shall be included in the bid.

2.  GENERAL:

The contractor should be well acquainted with the I.E. Rules 1956 as amended from time to time and with the Indian Telegraph Act 1889 so that the necessary provisions therein may be followed.

3.  SURVEY OF THE ROUTE:

The tentative Route Map of the line to be erected will be furnished by the APSPDCL to the Contractor along with the copy of the concluded agreement.

The contractor is required to carry out the detailed survey of the route of the line and fix up the locations at the average span indicated in the schedule and mark the locations and submit a detailed route map to the Engineer in charge of the work within 30 days for approval.  In the course of surveying by the contractor, any conspicuous variations in the change and physical feature to those indicated in route man and as actually existing as noticed, the deviations must be brought to be notice of the APSPDCL’s Engineer.  The APSPDCL’s Engineer if considered necessary shall make alterations to the route map and communicate the same to the contractor in writing. As such alterations shall be carried out accordingly and the APSPDCL’s Engineer after inspecting the surveyed route and the revised route map shall be given for final approval of the route map is given by the Engineer in charge in writing to the contractor.

- WAY LEAVES AND TREE CUTTINGS:

Proposals for way leaves and right of way shall be submitted by the contractor.  Permission will be obtained by the APSPDCL within reasonable time for which due notices shall be given by the contractor.  The Contractor shall arrange for tree cuttings or tree branches cutting also.

The width  of tree clearance to be adopted for the lines of various voltages are as detailed below:

- 11 KV line (Normal Line)

All growth within 4.572 M (15ft) on either side from centre line of support and all trees that may fall and foul the line.

In the case of beetle leaf garden all growth within 3.048 Meters (10ft.) on either side of the line.

- 11/33 KV (trunk lines):

All growth within 6.096 M (20ft) from the centre line of support and all trees which may fail and foul the line.

The contractor shall take all possible steps to see that standing crops etc., are not damaged while attending to tree cutting.  When such damage is inevitable the compensation will be borne by the APSPDCL provided the damage is with the prior concurrence of the Engineer.  The contractor shall bear the compensation for damage caused by the gangs without prior concurrence of the Engineer concerned.

No trees shall be cut until APSPDCL has made necessary arrangement with the authorities concerned and permission is given to the contractor to fell such tree.  The contractor shall arrange to remove the obstacles as soon as possible.

At time however, it may not be possible for the APSPDCL to arrange right-of-way for excavation of pole pits or erecting the poles or stringing the line.  At all such times, the contractor shall shift his gangs to other areas.  The rates quoted shall cover all such contingencies and no extra payments shall be claimed for such contingencies.

5.  EXCAVATION OF POLE /STAY/ STUT/ DP PITS :

    - After the final survey of the line and after marking the pole locations with pegs, excavation work has to be commenced in accordance to the approved route map.  Excavation is generally done by pick axes, crow V-bars and showers although some times earth augers are used.  Excavation of pole pits in very hard or rocky soil or in rock beds may involve blasting of rock by suitable explosives.  The pits for the supports are excavated in the direction of the line as this will facilitate the erection of support, in addition to giving greater lateral stability, the depth of the foundation to be excavated for pole shall be in accordance with relevant sketch for the erection of pole or stut/stays or D.P etc.

  - Excavation rates for poles, stuts/stays and D.P. pits shall be quoted by the contractor for the following types of soil including dewatering of pits and shoring and shuttering where ever necessary.  No quotation for extra rate for dewatering during excavation and shoring and shuttering will be entertained.

- All Soils other than hard rock.

B)  Hard-rock :  Hard – Rock will be that which requires drilling and blasting by any method.  The cost of drilling and blasting shall be included in the quoted rates.  In certain cases, when the area around the location happens to be an inhabited area consequent to which blasting cannot be resorted to, the excavation may have, to be dug with or by the process of drilling wedging, hammering and splitting or by the process of heating and splitting by sudden cooling.  The rate quoted shall take into consideration such contingencies also.  Whenever blasting is resorted to, the contractor shall make adequate arrangements of safety precautions.  The APSPDCL will not be responsible for any damages or accidents caused arising out of process of blasting.

NOTE:

- For soils other than hard-rock excavation rate to be quoted shall include back filling the pits with excavated soils after concreting where-ever necessary.

- For soils covered by hard rock variety, the excavation rate shall be including back filling with excavated rock bits and borrowed earth duly rammed after laying the designed rock foundation.

- No extra charges shall admissible for the removal of the fallen earth in the pit, when once excavated.

The quoted rates should cover all contingencies during the process of excavation.  For any reasons what- so ever, no extra claim will be accepted.

- FOUNDATION:

Classification of Foundation:

Depending on the type of soils, the subsoil water table and the presence of surface water, four types of foundation designs will be used for each locations classified in the following manner.

1)	Wet type:  To be used for locations:

- Where sub-soil waters is wet at 1.5 meters or more below the ground level.

- Which are in surface water for long period with water generation not exceeding one meter below the ground level eg. the paddy fields.

- In black cotton soils.

- Partially submerged type:

To be used at locations where sub-soils water table is met at more than 0.75 meters from the ground level.

- Fully submerged type:

To be used at locations where sub-soil waters is met at less than 0.75 meters from the ground level.

- Rocky type:

To be used at location where hard rock is met with and where the bond strength between the rock and the concrete will be very high.

7.  	ERECTION OF SUPPORTS

After the excavation of pits is completed the supports to be erected may be brought to the pit location.  Then the pole may be erected inside the pit.  Wooden support may be utilized to facilitate lifting of the pole at the pit locations.

Before the pole is put into the pit, RCC padding may be laid below the pole to increase the surface contact between the pole and the soil.  The padding will distribute the density of the pressure due to weight of the pole on the soil.

Having lifted the pole, the same should be kept in a vertical position with the help of manila rope of 25 mm dia using the rope as a temporary anchor.

As the poles are being erected say from the pole already erected to the next location where the pole is being erected the alignment of the poles are to be checked and set right by visual check.  The verticality’s of the poles are to be checked with a spirit level on both transverse and longitudinal directions.

Having satisfied that the vertically and alignment are all right earth filling or concreting is to be done.

In swampy and special locations, however, before earth filling, the poles are to be concreted up-to ground level of the pit.

After the poles have been set the temporary anchors are to be removed.  The supports shall be buried to a depth as per sketch enclosed.

8.	ERECTION D.P.STRUCTURES FOR ANGLE LOCATIONS (FOR 11 KV/33KV LINES):

Generally, for angles of deviation more than 200 double pole structures of spacing 1.2 mts (4 ft)may be erected.  The pits are to be excavated as per the bisection of the angle of deviation.

After the poles are erected, the horizontal/cross bracings should be fitted and the supports held in a vertical position with the help of temporary guys of manila rope at least 25 mm dia.  Ensuring that the poles are held in a vertical position (this can be checked with a spirit level) the concreting of the poles with cement, granite chips of size 20/30 mm mesh and sand in the ratio M400 (1:1:2) conforming to ISS is to be done from the bottom of the support to the ground level.  Before lifting the pole in the pit, concrete padding of not less than 75 mm thickness may be put for the distribution of the load of the support on the soil.

After the concreting is done, the pit may be filled with earth after the curing of the concrete is completed.

Four stays/stuts along the line, two in each direction and two stay/stuts along the bisection of the angle of deviation, are to be provided.

Stay/Stut concreting may be done with M 400 mixture.

The D. P. shall be erected as per the sketch enclosed.

9.  	ANCHORING AND PROVIDING GUYS FOR SUPPORTS:

Guys are to be provided to the supports at the following places (I) Angle locations, (ii) Dead end locations, (iii) Tee-off points, (iv)Steep gradient locations to avoid uplift on the poles.

The installation of guy will involve the following works:

- Excavation of pit and fixing of stay rod.

- Fastening guy wire to the support.

- Tightening guy wire and fastening to the anchor.

The marking of the guy pit for excavation, the excavation of pits and setting of the anchor rod must be carefully carried out.  The stay rod should be placed in the position such that the angle of inclination of the rod with the vertical face of the pit is as the case may be.  The concreting of the stay at the bottom should then be carried out.  The back filling and ramming must be well done thereafter, and allowed to set for at least 7 days.  The free end of the guy wire is passed through the eye of the anchor rod, bent back parallel to the main portion of the guy and bound after inserting the G.I. thimble.  The loop is protected by the G.I. thimble where it hears on the anchor rod.  Where the existence of guy wire proves hazardous, it should be protected with suitable asbestos pipe, filled with concrete, of about 2 mts. Length above the ground level, duly painted with white and black stripes so that it may be visible at night.  The turn buckle shall be mounted at the pole end of the stay and guy wire so fixed that the eye bolt turn buckle is half way in the working position thus giving the maximum movement for tightening or loosening.

Guy insulators are placed to prevent the lower part of the guy from becoming electrically energized by a contact of the guy when the conductors snap and fall on them or due to leakage.  No guy insulator shall be located less than 2.6 mts. from the ground.  The anchoring and providing guys for supports (Single guy Bow guy an fly guy) shall be done as per sketch 3 enclosed.  Bow guy and fly guy shall have to be provided as per the field conditions.

10.  	FIXING OF CROSS ARMS AND INSULATORS

After the erection of supports and providing guys, the next step would be mount the cross arms on the support.  The cross arm is to be mounted after the support is erected.  The lineman should climb the support having requisite tools with him and the cross arm is then tied to a hand line and pulled up by the ground man, through a pulley till the cross arm reaches the linemen.  The ground man should station himself well to one side so that if any material drops from the top of the pole it may not strike him.  All the materials required should be lifted or lowered by means of the hand line.  In no case, the material or the tools should be dropped or thrown from the pole top.

The fixing of 33 KV and 11 KV cross arms shall be in accordance to spacings detailed in Sketch G.I. bolts and nuts and spring washers of good quality only shall be used which have to be procured by the contractor.

10.1	Back Clamps:

The back clamps for fixing of the “V” cross arms will have to be procured by the contractor and shall be in accordance with sketch enclosed and the clamp shall be fabricated with 75 X 8mm M.S. flat for 33 KV and 50 X 8 mm M.S flat for 11KV.

  - Top Cleats:

The top cleat shall be got fabricated with M.S.channel of size 75X40 mm for 33 KV and 11KV and shall be in accordance with sketch enclosed.

11.  INSULATORS

The pins for insulators shall be fixed in the holes provided in the cross arms and the pole top brackets.  The insulators shall be mounted in their places over the pins and tightened.  In the case of strain or angle supports, where strain fittings are provided for this purpose, on strap of the strain fittings is placed over the cross arm before placing the bolts in the hole of the cross arms.  The nut of straps is so tightened that the strap can move freely in horizontal direction, as this is necessary to fix the strain insulator.

The insulators shall be cleaned and examined for defects before fixing.  It shall be ensured that all the current carrying parts are smooth and without dirt, cracks or chips.

- STRINGING OF THE LINE CONDUCTORS

For the guidance of the contractor certain Do’s and Don’ts are given below, before the workmen actually commence the stringing work.

12.1	Do’s and Don’ts

Do’s:

- Use proper equipment for handling aluminum conductors at all times.

- Use skids, or similar method for lowering reels or coils from transport or ground.

- Examine reel before unreeling for presence of nails or any other object which might damage the conductor.

- Rotate the reel or coil while unwinding conductor.

- Grip all strands while pulling out the conductor.

- Control the unreeling speed with a suitable braking arrangement.

- Use wooden guards of suitable braking arrangement.

- Use long straight, parallel jaw grip with suitable liners when pulling conductor thus avoiding nicking or kinking of the conductor.

- Use free-running sleeves or blocks with adequate groovers for drawing/paving conductors.

- Use proper sag charts.

- Mark conductors with crayons or adhesive tape of such (other) material which will not damage the strand.

- Make all splicing with the proper tools.

- Use a twisting wrench for twisting the joints.

- Chromite or graphite conducting oxide-inhibiting grease should be applied before cleaning with wire brush.

Don’ts:

- Do not handle conductors without proper tools at any stage.

- Do not pull conductors without ensuring that there is no obstruction on the ground.

- Do not pull out excess quantity of conductor than required.

- Do not make jumper connections on dirty or weathered conductor.  Clean the conductor using sand paper or wire brush.

- Do not handle aluminum conductors in a rough fashion but handle it with care it deserves.

12.2 	Conductor Erections

The erection of overhead line conductor is a very important phase in construction.  The erection of conductor’s can be sub-divided into 4 separate parts as follows:

- Transport of conductors to work site.

- Paving and stringing of conductors.

- Tensioning and sagging of conductors.

- Jointing of conductors.

At important crossing of roads, canals, navigable rivers railways etc., flagmen should be in attendance to ensure that normal services are not unduly interrupted.  These crossings should only be carried out in conjunction with and with the approval of the proper authorities concerned.

The conductor drums shall be transported to the tension point without injuring the conductor.  If, it is necessary to roll the drum on the ground for a small distance, it should be slowly rolled in the direction of the arrow marked on the drum.  The drum should be so supported that it can be rotated freely.  For this purpose the drum should either be mounted on the cable drum supports or jacks or hung by means of chain pully of suitable capacity, suspended from a tripod.  In case if it is not possible to raise the conductor drum by any of the above methods, a trench of suitable depth slightly bigger than the conductor drum may be dug, so as to facilitate free rotations of the drum when it is suspended in the trench by means of M.S.shaft.  While paving, care should be taken to see that conductor does not rub against any metallic fitting of the pole or on the bad/rocky ground.  Wooden trussels should be used for this purpose to support the conductor.

The conductor should be passed over the poles on wooden or aluminum snatch pulley blocks provided with low friction bearings.  While conductor is being paved out slowly, some braking arrangements should be made so that the rotation of the drum may be stopped in emergency.

In case the length of one piece of the conductor is less than the length of the section in which conductor paving is being done, it is easy to stretch one length of all phases from one end and the remaining length from another end of the section and thereafter jointing the two ends of the conductor where they meet on no account any part of the conductor shall be left at a height of less than 5 mtrs. Above the ground over night and the work shall be so arranged that before the end of the day, the conductor shall be raised to minimum height of 5 mtrs above the ground by rough sagging.

  - Mid Span Jointing of Conductors

The mid span jointing of conductors can be carried out by twisting joint.  As the ends of the wire should project a few centimeters, beyond the end of the sleeves.  The projected wires are given a sharp bend to keep them from slipping out of the sleeve.  The end of the sleeves are then held tightly by twisting wrenches and then given 4 to 5 turns in one direction generally anti-clock-wise direction.  Crimping tools are preferably to be used for joints and jumpers.

  - Sagging and Tensioning

On the completion of the paving of the conductors and making mid-span joints if any, tensioning operations will commence.  Temporary stays will have to be provided for both the anchoring supports in the section where the stringing has to be done.  At the tensioning end, one of the conductors is pulled manually upto a certain point and then come along clamp is fixed to the conductor to be tensioned.  The grip to the come along clamp is attached to double sleeve pully block or the pulley lift machine and gradually tensioned.

The conductor should then be sagged in accordance with the sag-temperature chart for the particular conductor and span.  The sag should then be adjusted in the middle span of the section.  The sag chart will be provided by the Engineer.

The stretch of the conductor has to be taken out before stringing in order to avoid the gradual increase in sag due to the setting down of the individual wires.  There are ways of accomplishing this.

- Pre stressing:

In this method the conductor is pulled up to a tension considerably above the correct figure, but never exceeding fifty percent of breaking load for a short period of say twenty minutes.  As this method requires more time and involves the use of stronger tackle to secure the higher tension the other method of over-tensioning is commonly adopted.

- Over tensioning:

This method consists of pulling up the conductor to a tension a little above the theoretical tension for the prevailing temperature and fixed it up at that tension with correspondingly reduced sag.  After a certain time the conductor will settle down to the correct sag and tension.  A tension of five to eight percent more than the theoretical value has been found to be suitable for the sizes of ACSR and AAAC conductors standardized by REC.  The ambient temperature during sagging may be recorded correctly.

Conductors can be sagged correctly only when the tension is the same in each span through out the entire length of the section.  Use of snatch blocks reduces the friction and chances of inequality of tension in various spans.

Sagging can be accomplished by several different methods but most commonly used method is “sighting”.  The sighting sag method of measuring sag is by the use of targets placed on the supports below the cross arms.  The targets may be light strip of wood clamped to the pole at a distance equal to the sag below the conductor when the conductor is placed in snatch block.  The lineman sees the sag from the next pole.  The tension of the conductor is then reduced or increased, until, the lowest part of the conductor in the span coincides with the lineman’s line of sight.

When sagging is completed, the tension clamps shall be fixed.  The clamp can be fitted on the conductor without releasing the tension.  A mark is made on the conductor at a distance from the cross arms equal to the length of complete strain insulator.  Before the insulator sets is raised to position, all nuts should be free.   Come along clamp is placed on the conductor beyond the conductor clamp and attached to the pulling unit.  The conductor is pulled insufficiently to allow the insulator assembly to be fitted to the clamp.  After the conductor is clamped to insulator, assembly unit may be released gradually.  If the tension is released with a jerk, an abnormal stress may be transferred to conductor and support, which may result in the failure of the cross arms, stay or pole in some cases.  After the stringing is completed, all poles, cross arms, insulators, fitting etc., are checked up to ensure that there have been no deformities etc.

The next step is to place the conductor on the top of the pin insulator from the snatch block and removing snatch blocks.  Conductors are then fastened to insulator by the use of aluminum wires.  The following points should be observed:

- Proper size of the binding wire which can be readily handled and with adequate strength to be used.

- The length of tie wire should be sufficiently long for making complete tie including the end allowance for gripping with the ends.

- A good tie should provide a secure binding between the line conductor and insulator and should reinforce the conductor on either side of the insulator.

- The use of cutting pliers for binding the site wire should be avoided.

- The tie wire which has been used previously should not be re-used.

Before tieing the conductor the insulator two layers of aluminum tape should be wrapped over the conductor in the portion where it touches the insulator.  The width and thickness of aluminum tape to be used for a specific size of conductors has been specified in handbooks of aluminum conductor manufactures and the same b preferred to.  The aluminum tapes should also be used at the tension clamp and for proper grip.

Normally in straight runs of line, the conductors are run on the top of insulators, when there is small angle of deviation the conductor is placed inside groove and binded.  Accordingly, there are two methods of tieing the conductors to insulators.  The binding wire/tie wire has to be procured by the contractor and the bid price shall include the cost of this.

  - The contractor shall entirely responsible for any damage to the supports, other accessories and conductor.  He shall also be responsible for proper distribution of the conductor drums to keep number and lengths of cut pieces of the conductor to a minimum.

  - Conductor damage and repair

If the conductor is damaged for whatever reasons and damage is not repaired aluminum sleeves etc., it shall be brought to the notice of the Engineer and shall not be used without his approval.  Even repairing of conductor surfaces shall be done only in case of minor damages, scuff marks etc.  Which are sage from both electrical and mechanical points of view.  The final conductor surface shall be clean, smooth, without any projections, sharp points, cut or abrasion etc., giving satisfactory corona and R.I performance.

  - No joint or splice be made in spans crossing over main roads, railways, small rivers or in tension spans.  Not more than one joint per conductor shall be allowed in one span.  The strength of the joint shall confirm to I.E rule 75.

  - Stringing rate:

The stringing rate for stringing of the conductor per route length of line shall include paving, stringing, clamping, jointing, tensioning and strain disc binding and clamping and fitting of all necessary accessories.  Wherever necessary ground clearance have to be measured to ensure obtaining adequate line clearance as per I.E. rule 77 (I).

- EARTHING

13.1	Pipe Earthing

At D.P. Location pits are to be excavated, the steel and metal parts are to be earthed by pipe earthling as per the drawing of sketch enclosed to this specification.  Duly filling the pits with finely broken coke having granule sizes not more than 25 mm thick, the coke shall be maintained up-to a distance of 300 mm from the pipe in all sides.  The top edge of the pipe shall be at least 200 mm below the ground level.  The steel strips shall be fixed not less than 300 mm deep from the ground level.

The tenders shall quote the charges for earthing inclusive of the cost of coke, excavation and back-filling.

  - Pole earthing : Supports shall be properly earthed.

- CROSSINGS

Guarding shall be erected as per standards and as per sketch a, b, c, enclosed for Railways, telephone lines and power lines.

EXECUTION OF WORKS RELATING TO POWER LINE CROSSINGS AND RAILWAY CROSSINGS:

Work such as erection of support underneath an existing power line and paving out of conductors and earth-wire and stringing the power line crossing span or a railway crossing span, will have to be done only after receipt of line clear form APSPDCL authorities and approval from the concerned officer, which some times, may not match with program of the contractor.  In such cases, the contractor shall execute such works as and when approvals are received.  His rates for line erection and stringing shall take into consideration such contingencies also.

- CONCRETING

15.1	The cement concrete used for the foundation shall be of M 400 grade.

The sand used for the concrete shall be composed of hard silicon materials and well sieved.  It shall be clear and a sharp angular grit type of and free from earthy or organic matter and deleterious salts.

The aggregate shall be of clean broken hard granite or other stone specified or approved by the Engineer.  It shall be hard, close grained quality.  It shall also be as far as possible cube like preferably angular, but not flaky, perfectly clean and free from the earth organic or other deleterious matter, 38 mm aggregate shall be of size as will pass through 38 mm square mesh measured in the clear.

The Water used for mixing concrete shall be fresh and conform to ISI it should be clean and free from oil, acids and alkali.  Saltish or brackish water should not be used.

The concrete should be mixed as stiff as the requirements of placing the concrete in the forms or moulds with as and the degree to which the concrete resists segregation will permit.  Hence, the quantity of water used should not be too much.

Proper forms of moulds adequately braced to retain proper shape while concreting should be used.  The mould should be made water tight so that cement cream will not come out leaving only sand and jelly consequently forming honey-combing in the concrete.  The rate for concrete should be made so that the works are not held up on this account.

After concerting to the required height, the top surface should be finished smooth, with slight slope towards the outer edge to drain off the rainwater falling on the copings.  These copings and muffings should be done after the stringing is completed in respect of tension locations and such other locations as may be decided by the Engineer at site.  For such locations an adhoc reduction of Rs.100/- per location will be made while billing for concrete and this will be released after the coping and muffing are completed.

In wet locations, the site must be kept completely dewatered both during the placing of the concrete and for 24 hours after completion.  There should be no disturbance of concrete by water during this period.  No extra rate will be paid for the dewatering and the rate for concrete shall be inclusive of dewatering charges.

The forms of moulds shall not be removed before a lapse of about 24 hours after the completion of concreting.  After removal of the form moulds, the concreted surface, wherever required, shall be repaired with a rich cement and sand motor in the shortest possible time.

  - The full concreting for the poles if erected in excavated pit shall be done so that the complete block will be of the dimensions (0.6X0.6X1.6) + 0.2X0.2X0.2 Mts (0.6X0.6X1/35) + 0.2X0.2X0.2 Mts. so as to maintain an exposed portion for 0.2 meters height above the ground level.

  - If augur is used for making pole pits, ramming shall be done after erection of pole.

16.	WORKMANSHIP

The contractor shall entirely be responsible for the correct erection of all support as per the approved drawings, and their correct setting and alignment, as approved by the Engineer.  If The supports and D. P. structures after the erection are found to differ from approved route maps and drawings or to be out of alignment, the contractor shall dismantle and re-erect them correctly at his own cost without extension of time.  The supports must be truly vertical and in plumb after erection and so straining will be permitted to bring them to vertical position.  Vertically of each support shall be measure by the contractor and furnished to the Engineer.

17.	Location numbers for each pole shall be painted on the pole.  The rate for pole erection shall be inclusive of painting the Locations numbers of all the poles.

Anti-climbing devices, and danger boards are to be provided at all railway crossings and road crossings.  No extra charges shall be admissible even though separate gangs may have to be sent by the contractor for fitting these accessories and attachments on the support at the appropriate time.

18.	FINAL CHECKING, TESTING AND COMMISSIONING

After the completion of the works final patrolling and checking of the line shall be done by the contractor to ensure that all the foundation works, pole erection and stringing have been done as approved by the Engineer, and also to ensure that they are complete in all respects.  Contractor shall prepare pole schedules and hand it over to the Engineer.  All works shall be thoroughly inspected keeping in view of the following main points.

- Sufficient back filled earth is lying over each foundation pit and it is adequately compacted.

- Concreting and coping of poles are in good and finally shaped conditions.

- All the accessories and insulators are strictly as per the drawings and are free from any defects or damages, what-so-ever.

- All the bolts and nuts should be G.I.material and as per contractual provisions.

- The stringing of the conductor has been done as per the approved sag and desired clearances are available.

- No damage, minor or major to the conductor, earth wire, accessories and insulator strings will unattended are noticed.

- For all points double jumpers shall be provided to each phase.  The jumpers provided at the cut points are connected rigidly to the tension hardware utilizing all the jointing bolts provided for the purpose.

The contractor shall submit a report to the above effect to the Engineer.  In case, it is noticed later that some or any of the above are not fulfilled the engineer will get such items rectified through other agencies and recover the cost of such works from the bills payable to the contractor against that contract or any other contract executed by him for the APSPDCL

After final checking, the lines shall be tested for insulation in accordance with tests prescribed by the Engineer.  All arrangements for such testing or any other test desired by the Engineer, shall be done by the contractor and necessary labour, transport and equipment shall be provided by him.  Any defects found out as a result of such tests, shall be rectified any the contractor, forthwith, without any extra charges to the APSPDCL

In addition to the above, the contractor shall be responsible for testing and ensuring that the total and relative sags of the conductors are within the specified tolerance.  Such tests shall be carried out at selected points along the route as required by the Engineer and the Contractor shall provide all necessary equipment and labour to enable the test to be carried out.  After satisfactory tests on the line and approval by the Engineer the line shall be energized at full operating voltage before handling over.

19.	SUPPLY OF MATERIALS BY APSPDCL

The material to be supplied by the APSPDCL will be delivered at APSPDCL stores nearby.  The contractor is responsible for handling, storage, and maintenance and safe custody of the materials from the time of taking over until the date of issue of completion certificate.  No handling transport or storage charges shall be paid by the APSPDCL  to the contractor for the materials supplied by the APSPDCL  for erection.

19.1	Supply of materials by the contractor:

The contractor has to make his own arrangements for procurement, supply and use of materials as per Annexure – 1A and compliance of the following should be ensured.

- These materials should conform to the relevant Indian Standard specification.  These materials shall be supplied at-least one month in advance of their requirement manufactures test certificate for these materials shall be submitted and got approved by Engineer before utilization.  The materials so supplied by the contractor shall be guaranteed by him for satisfactory performance up-to the end of the maintenance and defects liability period.

- All materials to be supplied should fully conform to provisions under clause 3 of Instructions to Bidders.

- In procurement of these items the contractor shall follow all regulations of the APSPDCL/Government of India in respect of import license etc., if he chooses to procure these from imports.  Further, the contractor shall be responsible for the payment of applicable duties and taxes, port clearance inland transportation etc.

- The materials for which advance is given by APSPDCL is to be insured by the contractor at his cost from the date of payment of advance to the date stated in the certificate of completion for the whole of the works.

- INFORMATION AND DATA:

- The information furnished is the best available however, the APSPDCL does not guarantee the correctness or interpretations, deductions or conclusions which are given as supplementary information in the Bid Documents or in any reports, maps, drawings, diagrams or in other reference information available to the bidder from the APSPDCL  of or otherwise.

The information have been produced as found, communicated to ascertained or otherwise learned by the APSPDCL

- It will be the Bidder’s responsibility to satisfy himself from the “Reference Information” supplied and or inspection of the site that sufficient quantities of construction materials required for the works shall exists in the designated borrow areas or quarry sites.

The APSPDCL does not accept any responsibility either in handling over the quarries or procuring the materials or any other facilities.  The Tenders will not be entitled for any extra rate or claim for the misjudgment on his part for the quantity and quality of materials available in the quarries.

- Failure by the Bidder to have done all the timings which is inaccordance with this condition he is deemed to have done shall not relieve the successful Bidder of the responsibility for satisfactorily completing the works as required at the rates at the rates quoted by him.

21.	CONSTRUCTION MATERIALS

21.1	Cement:

The contractor has to make his  own arrangements for the procurement of cement to required specifications required for the works subjected to the followings:

- The contractor shall procure cement, required for the works only from reputed cement factories (Main producer) acceptable to the Engineer –in-Charge.  The contractor shall be required to furnished to the Engineer –in-Charge bills of payment and test certificates issued by the manufactures to authenticate procurement of quality cement from the approved cement factory.  The contractor shall make his own arrangement for adequate storage of cement.

b)	The contractor shall procure cement in standard packing of all 50Kg per bag from the authorized manufacturers.  The contractor shall make necessary arrangement at his own cost to the satisfaction of Engineer-in-Charge for actual weighment of random sample from the available stock and shall conform with the specification laid down by the Indian Standard Institution or other standard foreign institutions as the case may be, Cement shall be got tested for all the tests as directed by Engineer-in-Charge at-least one month in advance before the use of cement bags brought and kept in site Godown.

Cement bags required for testing shall be supplied by the Contractor free of cost.  However, the testing charges for cement will be borne by the APSPDCL.  If the tests prove unsatisfactory, then the charges will be borne by the Contractor.

c)	The Contractor should store the cement of 60 days requirement at least one month in advance to ensure the quality of cement so brought to site and shall not remove the same without the written permission of the Engineer-in-Charge.

The Contractor shall forthwith remove from the works area any cement that the Engineer-in-Charge may disallow for use, on account of failure to meet with required quality and standard.

- The contractor shall further, at all times satisfy the Engineer-in-charge on demand, by production of records and books or by submission of returns and other proofs as directed, that the cement is being used as tested and approved by Engineer-in-charge for the purpose and the Contractor shall at all times, keep his records up to date enable the Engineer-in-charge to apply such checks as he may desire.

- Cement which has been unduly long in storage with the Contractor or alternatively has deteriorated due to in adequate storage and thus become unfit for use in the works will be rejected by the department and no claim will be entertained.  The Contractor shall forthwith remove from the work area, any cement the Engineer-in-charge may disallow for use on work and replace it by cement complying with the relevant Indian Standards.

  - STEEL:

The Contractor shall procure mild steel reinforcement bars, high yield strength deformed (HYSD) bars, rods and structural steel etc., required for the works, only from the main or secondary producers manufacturing steel to the prescribed specifications of Bureau of Indian Standard or equivalent and licensed to affix ISI or other equivalent certifications, marks and acceptable to the Engineer-in-Charge necessary ISI, list certificates are to be produced to Engineer-in-Charge before use on works.  The unit weight and dimensions shall be as prescribed in the relevant Indian standard specifications of steel. The steel shall be painted with two coats of red oxide and two coats of aluminium paint.

- WASTAGE:         DELETED

Note: The Contractor has to follow R.E.C. standard for the works wherever it is not specifically mentioned above.

SECTION – 5A

TECHNICAL SPECIFICATIONS FOR SUBSTATION WORKS

- SCOPE:

The scope of the specification covers the following:

- Civil works in the switchyard as per para 1.1

- Construction of control house as per para 1.2

- Erection of structures, bus bars, etc., equipment in switchyard

And control room as per para 1.3.

- Electrification of control house as per para 1.4

- Supply of materials as per para 1.5

  - Civil Works in Switchyard

- Excavations for

- Foundations, etc.

- Retaining wall

- Leveling

- Cable laying, earthing.

- Cement Concrete foundations for structures, transformer, Station transformers Plinths.  Foundation bolt type for other equipment / structures.

- Leveling of sub station site with borrowed earth of gravel or excavated earth.

- Peripheral fencing / compound wall

- Construction of cable ducts including cable ducts, crossing control room wall etc.,

- Formation of roads.

  - Control House

The work involves providing foundations, plinth beam, columns and beams for super structures, laying R.C.C. Slab, providing doors, windows, flooring with polished stone, painting providing water and sanitary arrangements etc.

  - Erection Works

- Erection of main and auxiliary structure and equipment including panels.

- Stringing of bus, jumpering, connections between equipment buses etc.

- Earthing system including laying of C.I. popes and B.H. Coke for earth pits.

- Cable laying and terminations including erection of marshalling boxes.

- Illumination of switchyard.

  - Electrification of Control House

The work involves electrification of control room.

  - Supply of Materials

WORK ON TURNKEY BASIS

- NUMBERING OF SUPPORTS AND NAMING OF FEEDERS

Each support shall be numbered serially commencing from the 33 KV incoming Bay, on the support itself, indicating the number of support with red colour.

Each 33 KV and 11KV feeders shall be named on the name plate of size 100 X 300 mm, manufactured out of 16 gauge steel, enameled red on white enameled back ground.  The letters, numbers should not be less than 45 mm high.  The back side of the plate should be enameled black.  Two number 12 mm dia bolts and nuts shall be supplied with each name plate for fixing the same symmetrically on the support at about 3 meters above ground level.

- PHASE PLATES

The set phase plates comprising red, yellow and blue shall be provided on each of the bays.  The phase plate shall be of minimum 1.6 mm thick mild steel sheet.  Back of the plates shall be enameled black.  The phase plate shall conform to IS 5613 (Part II/Sec 1) 1976.

- DANGER BOARDS

Danger Boards shall be provided and these danger boards shall conform to the standards given in IS 2551 / 1963.

The materials that will be supplied to the Contractor for utilization on the connected works of Substation is as per Annexure 2A of Section 5A, and the Contractor has to arrange their transport and handling.

  - Type of Construction

The Substation structures are of 152 X 152 mm fabricated R. S. joists / 9.5Mtrs. Long.  The foundation of structures are cement concrete/mass concrete type.  The 33 KV and 11 KV bus are Strung with 200 Sq. mm AAA Conductor.  A control house to locate panels, battery, battery charger and DC-Distribution Board is to be constructed.

  - Site Layout

A copy of the site lay out of the Substation is enclosed to give an idea about the work involved to the bidder.

  - Drawings

The drawings referred to below shall form part of the specification.

- Switchyard layout. b) Control House Plan. c) Peripheral fencing drawing.

- EXECUTION OF CIVIL WORKS

  - Cleaning up the site.

During construction the contractor shall keep the work site and storage area used by him free from accumulation of waste materials or rubbish and before completing the work the contractor, shall, at his own cost, remove or dispose off in manner satisfactory to the Engineer in charge.  All temporary structures, waste and debris shall be cleared, all holes in the ground shall be filled in and the land restored to its original state as far as is practicable and the entire premises should be kept in a neat and tidy condition of cleanliness as the Engineer may direct.

Any damage done to the permanent or temporary works to the Department by the Contractor or his sub-contractor shall be made good at contractor’s expense.

2.2	Paras 2.3 to 2.10.16 referred hereunder are applicable to all civil works under the specification including control House.

2.3	Excavation

The clause covers excavations to be done for all the civil works, such as laying foundations for structures, equipment, retaining wall, buildings (Control Room) etc.  Excavation rates quoted shall be inclusive of dewatering, shoring and shuttering required if any.

Separate rate is to be quoted for excavation in hard rock requiring blasting.  Blasting material required if any has to be procured by contractor himself.  Necessary assistance in the form of approval for procurement of the material will be given by the APSPDCL to the extent possible.  All rules under Explosive Act shall be followed by the Contractor.  Blasting work shall be done only after approval by the site Engineer during specified hours.  The rate for excavation in hard rock shall cover costs of all the required materials and labour.  The person in-charge of blasting shall have blast exploded before working people are permitted to re-approach work site.  Withdrawal of unexploded charge will not be permitted under any circumstances.  Unexploded charge shall be flooded with water and the hole marked in a distinguished manner.  Another hole shall be drilled at a distance of about 450mm of old hole in direction of un-exploded charge and fired in usual way.  This process shall be continued till the original blast in exploded.  Excavation in decomposed or soft rock shall be carried out by crowbars or Pick-axes or pneumatic drill etc.  If he desires to do blasting, he shall obtain permission of site Engineer and do accordingly but payment will be done at normal soil rate only.  The rock obtained during excavation is the APSPDCL’s property and it shall not be used under any circumstances by the contractor. Rock excavated shall be stacked by the successful bidder at a convenient place within the Substation premises as directed by the Site Engineer at no extra cost.

  - Back filling

After completion of foundation, footings and wall and other construction below the elevation of the final grades and prior to back-filling, all forms, temporary shoring, timber, etc., shall be removed and the excavation cleaned of all trash, debris and perishable materials.  Back filling shall begin only with the approval of the Engineer-in-charge.

Back filling shall be done with inorganic materials obtained from the excavation of borrow pits, if suitable, and subject to the approval of the APSPDCL’s Engineer-in-charge.

Back fill shall not be dropped directly upon or against any structure or facility where there is danger of displacement or damage.

Backfill shall be placed in horizontal layers not exceeding 15cm. in thickness. Each layer shall be compacted with proper moisture content and with such equipment as may be required to obtain a density equal to or greater than 94% of maximum as determined by the relevant India Standards.  Trucks or heavy equipment for depositing or compacting back-fill shall not be used within 1.5 meters of the foundation / structures, or other facilities which may be damaged by their weight or operation.  The methods of compacting shall be subject to approval of the Engineer-in-charge.

Backfill adjacent to pipes shall be free of stones, concrete, etc. compacted uniformly on both sides of the pipe and where practicable, to a depth of 300mm over the top of pipes.  When tamping around piping care should be taken to avoid unequal pressures.

  - Technical Specifications

2.5.1	Material & Quality:

All the material used in the works shall be of the best quality of their respective kinds and specified herein.  They shall be obtained from sources and Contractors approved by the Engineer or his representatives, and shall comply strictly with the tests, specified herein after or, where tests are not specified in this specification, they should conform to the requirements of the latest issue of the relevant Indian Standards herein after abbreviated to as (I. S) or other approved National Standards authorized by the Engineer.

    - Inspection and Testing:

All the materials used in the works shall be subject to inspection and tests if required by the Engineer.  Unless otherwise stated, the costs of all tests required by this specification shall be deemed to be included in the rates and prices named by the contractor in the bill (Schedule) of quantities.

    - Any material which is prepared or manufactured without notice having been given in writing to the Engineer may be rejected if the Engineer considers that his inspection was necessary during the process of manufacture of such material.

2.5.4	Approvals: No material shall be used in the works unless it has first been approved by the Engineer or his representative.

2.5.5	Aggregates: The aggregates such as sand and hand broken granite metal shall be obtained as per the samples approved by the Engineer.  The cost of coarse and fine aggregates along with bricks and concrtete blocks shall be included in the rates of items of all the civil works referred to in schedules of Section 6 of the specification.  The coarse aggregate refers to HBG metal of various sizes and fine aggregate refers to sand.

2.5.6.	Indian Standards: The aggregates both fine and coarse shall comply with the requirements of I. S. 456 for concrete aggregates and I. S. 383 for sand for use in concrete, plastering and mortar except as hereinafter stated and shall be delivered to and maintained at the site, clean, washed and free from dirt.

2.5.7.	Samples: Samples shall be submitted to the Engineer and all aggregates used in the work shall be at-least equal to the approved samples.

2.5.8.	Fine Aggregate: The fine aggregate for concrete, shall consist of naturally occurring sand graded in accordance with requirements of I. S. 383 for grading Zone – 2 or grading Zone – 3 except that no particle shall exceed 3/16 inch.           It shall be free from excessive sharpness.  Fine aggregate to be used in cement mortar and in plastering shall comply with I. S. 383.

2.5.9.	Coarse Aggregate: Coarse aggregate shall be graded to produce sound concrete and for reinforced concrete shall be such that at least 5% by weight will pass through a mesh of a size ¼ inch less than the minimum lateral distance between the reinforcing bars or ¼ inch less than the minimum cover, which ever is smaller.

2.6  	Water For Concrete

Clean fresh water shall be used for mixing concrete and mortar and curing.  The water used for mixing and curing shall be free from deleterious matter and acids and alkaline substances in a solution or suspension.  Potable water shall be used for mixing concrete.

2.7      Cement (See Clause 21.1)

2.8	Reinforcement

    - Steel required for reinforcement shall be supplied by successful bidder.  The contractor shall work out the requirement immediately after taking over the site and receipt of working drawings.  The cost of reinforcement steel, binding wire and fabrication charges for all the works shall be included in corresponding item of such schedules.

  - Concrete

This clause is applicable for all the civil works under this specification.  Rate of concrete shall include cost of shoring, shuttering and dewatering wherever necessary.

2.9.1	Code of Practice:  Except where otherwise specified described or directed all concrete and reinforced concrete work shall be carried out in accordance with IS 456, Code of Practice for plain and reinforced concrete.

2.9.2	Gauging Concrete:  Aggregate shall be measured in proper gauge boxes.  When measuring the fine aggregate due allowance shall be made for the moisture content and the bulk adjusted to suit the mix.  The methods adopted for gauging the concrete materials shall have the approval of the Engineer.

2.9.3	Concrete Proportion:  Concrete shall be normal mix as specified in the drawings or in bill/schedule of quantities

2.9.4	Consistency: The quantity of water used shall be sufficient to produce a dense concrete of adequate workability for the purpose, and will surround and properly grip all the reinforcement.

2.9.5	Crushing Strength: The crushing strength of the concrete should be as specified in I. S. 456 for the desired mixes.

2.9.6	Gauging Water:  The General arrangements for the supply of water for mixing concrete shall be to the satisfaction of the Engineer who will determine the quantity of water to be employed in the mix according to the degree of moisture in the aggregate.  The quantity of water thus determined shall be accurately measured for each separate mixing in a suitable container.

2.9.7	Mixing Concrete: Concrete shall be thoroughly mixed to a uniform consistency in the mixing machines of approved types.  Mixing shall continue until the cement is thoroughly distributed throughout the mass, and shall last at-least two minutes or for 80 turns of the mixer after the whole of the water has been added.  Any concrete showing signs of initial setting before being deposited shall not be used in the works and shall be removed from the site.

    - The concrete shall be discharged from the mixer on to a level watertight platform or floor or into a watertight receptable.

    - Normally hand mixing of concrete will not be allowed be allowed but where the total quantity of concrete is considerably small, the mixing may be done by hand subject to the approval and entirely at the discretion and satisfaction of the Engineer.

2.9.10	Concreting in Unsuitable Weather:  In the event of rain, storms or other severe weather conditions arising, concreting shall be stopped and appropriate temporary stop ends vee-grooves etc. placed as may be necessary.  To meet such circumstances, the contractor shall always have in readiness on the site approved framed sheeting, tarpaulins etc. for the protection of newly placed concrete.  Should any concrete be damaged due to rain, storms or other weather conditions, the Engineer may order the cutting out/replacement of the damaged concrete at the expense of the contractor.

2.9.11	Form Work: This clause is applicable for form work / centering etc. for all the civil works under the specification.

2.9.12	The form work shall conform to Clause 10 of I. S. 456.  The contractor shall be entirely responsible for the sufficiency and efficiency of the form work, which in turn includes moulds, and also for the safe removal of the same.  Before commencing the work he shall submit for the approval of the Engineer, details of the form work he proposes to use but such approval shall in no way relieve him of any of his responsibilities for the sufficiency and efficiency of the work.  The form work shall be resistant to the strains imposed on it, while vibrating the concrete and shall retain all the fines in the concrete as may be necessary to provide the desired concrete surface.

2.9.13	The form work shall be designed and arranged so that it will not settle under the load and can be stripped and removed without causing any blemish or jar to the concrete.

2.9.14	All forms shall be securely braced and supported to prevent any sagging or bulging during construction.  In no circumstances shall wire ties be used.  Camber, radius strips, Liners and cores shall be provided where necessary and shall be true to space and securely fixed.  All forms shall be fixed to the proper line and trued up immediately before depositing the concrete.  All joints shall be close enough to prevent leakage of water from the concrete.

2.9.15	From work for all exposed faces of mass concrete and for all faces of reinforced concrete shall consist of approved material so finished as to produce the concrete surface finish specified without any loss of fines and without honeycombing, bulges etc, Strutting shall be of such design as to allow accurate adjustment and easy removal.

2.9.16	Shuttering of form work against the sides of the structure which is subject to movement or vibration will not be permitted.

2.9.17	The inside faces of the forms shall be treated with mould oil or other approved preparation.  The treating material shall not have deteriorating effect on concrete as well as form work.  The treating material shall not come into contact with the reinforcement.

    - Removal of Formwork: The length of time between concreting and the removal of the form work is the sole responsibility of the contractor.  It shall, however, be competent, to the Engineer to require a minimum length of time.  For structure foundation minimum time limit specified is 24 hours for removing form work from date of placing concrete.

    - Stop Ends: The position of temporary stop ends for vertical joints shall be as approved by the Engineer.  Shuttering to form the stops shall be firmly fixed and secured round the reinforcing bars.  Such concrete as passes through the stop shall be hacked off and removed as soon as the concrete has set.

  - Construction Joints: Recesses of approved size and type shall be formed in construction joints where required by the Engineer in order to form as key with the following concrete.  The cost of all shuttering to construction joints shall be deemed to be included in the rates named in the priced bill of quantities (Schedule of quantities)

2.10.1	Before depositing any concrete resting or abutting on work previously carried out the surfaces and ends of the existing work shall be thoroughly hacked to such an extent that no portion of the previous surface remains.  Thus roughened surfaces shall be thoroughly cleaned off, brushed, and watered immediately before the succeeding operations are commenced.  The roughened surface shall be coated with cement mortor ½ inch thick immediately before the concrete of the next layer is placed (special care shall be taken to put the mortor and fresh concrete thoroughly up against the hardened concrete)

2.10.2 Cleanliness of Form Work: Before concreting is commenced all form work shall be scrupulously cleaned and wetted, and the contractor shall adopt all necessary measures to ensure that all debris, dirt, wash water and other refuse is removed.  The reinforcement and form work then be inspected by the Engineer and concreting shall not be commenced until the Engineer gives permission.  Such inspection shall not however relieve the contractor and of his responsibilities for the correctness of the work in every respect.

    - Execution of Concrete Work : Concreting shall be carried out in sections, not exceeding the limits specified for particular work.

    - Casting Programme : The contractor’s casting programme shall be such that such section of work can be satisfactorily completed in one operation after permission has been given to proceed.  No claim for overtime working for completing a casting programme will be entertained.

    - Conveyance of Concrete: The concrete shall be conveyed from the mixer to its place in the works as rapidly as possible and in such a manner that there shall be no separation or loss of the ingredients.  In no circumstances shall more than half an hour lapse between the time when water is added to the mix and time when the concrete is finally consolidated in position. The use of concrete distributing chutes at an angle of more than 45 degrees from the horizontal will not be permitted without the prior written sanction of the Engineer.  In no case shall concrete be dropped from barrows or otherwise from a height of more than one and half meters. The arrangements to be adopted by the contractor for conveying and depositing concrete shall be subject to the approval of the Engineer.

    - Depositing Concrete: Before any concrete is put in, the contractor shall carryout any filling of pockets or trimming the sides where found necessary to suit the level and line of the concrete to be laid as directed by the Engineer at site.

Concrete shall be placed in one operation.

    - Consolidating Concrete: Concrete normally shall be consolidated by means of sufficient number of mechanical vibrators.  Hand ramming and tamping will only be allowed where specified or with the prior permission of the Engineer.  Hand ramming and tamping where permitted shall be sufficient and efficient so as to produce uniform consolidation.

    - The concrete shall be thoroughly worked all round reinforcement and against shutters so that all enclosed air is duly expelled and the concrete surface when stripped be found to be good and free of the formation of air pockets, honey combing or other defects.

    - The concrete shall be worked into position where placed and not allowed to flow.  For sloping beams the work of depositing concrete shall start from the lower end and work upwards.

2.10.10 Except where arrangements approved by the Engineer are made for placing concrete under water, the areas on which concrete is to be deposited shall be made and kept free from standing water during concreting operations and running water crossing or entering such areas shall be brought under control before concreting is commenced.

2.10.11Finish of Concrete Surface :  Immediately any wrought or metal faced form work is struck the surface of the concrete will be inspected by the Engineer and after any remedial work directed or permitted by the  Engineer has been completed to his satisfaction,  the contractor shall remove all form marks and other imperfections in order to give uniform appearance.  The cost of this work shall be included in the rates for concrete.

2.10.12Floor surfaces shall be worked to a smooth-even-finish to correct levels of falls as indicated in the drawings or as directed.

2.10.13 Where so directed, concrete floor surfaces shall be treated with silicate of soda grade P.84 diluted with four times its volume of water applied to the work with a watering can or spray and afterwards spread evenly with a mop or brush.  Twenty-four hours later a second application shall be made and, if any surface still appears porous, further application of the solution shall be given until the work will absorb no more.  Any excess liquid on the surface after the last coat has been absorbed shall be removed, and the surface allowed drying.  When dry it shall be washed with the plain water.

2.10.14Curing: The curing period shall commence immediately after the concrete is finally trowelled or screeded and continued for a period of 14 days for switchyard structure foundations and for other civil works period shall be 21 days.

The top and side surfaces of concrete shall be kept moist and be protected from the direct rays of the sun during the period.  The Contractor shall submit to the Engineer his proposals for ensuring continuous protection of the concrete during the curing period.

2.10.15Defective Work: Concrete which is defective from any cause whatsoever shall, if so directed by the Engineer, be cut out and the work reconstructed at the contractor’s cost. No concrete thus cut out shall be reused.

2.10.16The faces of the concrete work shall be sound and solid, free from honeycombing.  No ‘Patching’ of any concrete facing will be allowed without the written permission of the Engineer.

  - Reinforced Concrete

2.11.1 Reference shall be made to clause 2.8.1 for the cost of reinforcement steel, binding wire and labour charges. The proceeding clauses relating to concrete generally shall be read in conjunction with the following.

2.11.2	Mixes: The mixes of concrete shall be as specified in the bill (Schedule) of quantities or shown in the drawings.

2.11.3	Cover to reinforcement: The reinforcement shall in all cases be covered with no greater and no less than the minimum thickness of concrete specified as shown in the drawings.  Where two bars cross, the outer should have the minimum cover and no more.

2.11.4 Form Bolts: Any form bolts that are in the concrete shall be withdrawn when the forms are stripped. They shall not be placed within 50 mm of any steel reinforcement, so that the holes they leave do not reduce the effective cover on the steel.

    - Bending Reinforcement: Bends or other labours on reinforcing bars shall be carefully formed exact in accordance with the drawings, otherwise, all bars shall be truly straight.  Bends shall be made cold round a former having a diameter   at-least four times the diameter of the bars.  Heating of bars for any purpose whatsoever will not be allowed.

    - Splicing Reinforcement: Where splices or overlapping in reinforcement are required the bars shall be provided with such splices or overlaps as are shown in the drawings. No bars may be jointed by welding unless special permission in writing has previously been given by the Engineer.  While applying for such permission the contractor shall supply full details of the method he proposes to use.

    - Fixing Reinforcement: The number, size, form and position of all steel reinforcing bars, ties, links, stirrups and other parts of the reinforcement shall be exact in accordance with the drawings, and such parts shall be kept in the correct positions in the forms without displacement during the process of working the concrete into place.  Space bars, supporting stools and distance pieces to maintain the reinforcement in the correct position shall be provided by the contractor as directed by the Engineer, without any extra cost to the Board.

    - The use of timber blocks for welding the steel of the forms will not be permitted.

    - All straight bars shall be fixed parallel to each other and to the sides of the forms.  Any ties, links or stirrups connecting the bars shall be tied so that the bars are properly braced.  The inside of their curved parts shall be in actual contact with the bars round which they are intended to fit.

2.11.10 Binding Wire: Bars shall be bound together with black annealed steel wire No.  16 S.W.G. thick and the binding shall be done tight with proper pliers or automatic binders.  The free ends of the binding wire shall be sent in walls.  The rate of reinforcement should be inclusive of cost of binding wire.

2.11.11 All steel reinforcement before the concrete is deposited shall be clean and free from all loose mill scale, dust and loose rust, and coatings such as paints, cement, grout etc.

2.11.12 Depositing: No concrete shall be deposited until form work and reinforcement has been inspected and approved by the Engineer.  Care shall be taken that the steel reinforcement is thoroughly surrounded by the concrete and that no voids or cavities are left.  Consolidation of the concrete, either by hand or mechanical vibration, shall be to the satisfaction of the Engineer, and under no circumstances shall consolidation be obtained by heavy impact on the form work.

2.11.13 The top of each layer of concrete shall be laid parallel to the longitudinal axis of the work and shall not be at a slope to it.

2.11.14 Defective work: If, on the removal of the shuttering any honeycombing or other defective workmanship is found in the face of the concrete, the Engineer will decide whether, in his opinion, the strength of the member is affected, and whether ‘patching’ shall be permitted in which case the defective concrete shall be cut out to the extent ordered by the Engineer, and the remaining concrete thoroughly cleaned and made good.  If before or during this operation, any reinforcing bar is exposed, the cutting out shall continue right round the bar, to form a key.  Where reinforcing bars are so exposed, care shall be taken to ensure that they are not damaged by the tools used for cutting out the concrete.

2.11.15 If, in the opinion of the Engineer, the strength of the member is affected by the defective materials or workmanship, he may direct that the whole member shall be removed and a new member constructed by the contractor without charge.  The contractor may however, elect to carry out load test at his own cost, and if the load test shows results sufficiently satisfactory to the Engineer, the member may be left in place, provided all surface defects are made good by the contractor without charge.  The weight of the test load will be determined by the Engineer.

2.11.16 If ‘Patching’ is discovered which has been carried out without the permission of the Engineer the whole member affected will be liable for rejection, in which case the member shall be removed and a new member constructed by the contractor, all without charge.

2.11.17 Scaffolding: The rates quoted by the bidders for all civil works shall be inclusive of scaffolding charges required if any.  Materials and labour required for scaffolding shall be arranged by the contractor himself.

2.12.	Levelling: Sub-Station switchyard should be levelled as per directions of Engineer with the surplus earth left over after back filling the structure foundations.                 If surplus earth is not adequate for leveling, the switchyard is to be levelled by supplying gravel or any other soil.

  - Excavations and foundations for Structures and Transformer Plinths: Foundations

for structures and transformers and VCB plinths and Station transformer shall be

erected as per the sketch enclosed.  The retaining wall/compound wall foundation

shall also be as per sketch enclosed.

2.14.A Laying of Hume Pipe in Road Crossing: When a cable has to cross a road, it has to pass through hume pipe of suitable size as approved by the Engineer.

2.14 B	Cable duct in Control Room: The cable duct of size 600 X 450 mm is to be constructed as per the directions of Site Engineer.

2.14 C	Cable Trench in Switchyard: The cable shall be laid in the trench of size 600 mm depth and 450 mm width by providing 12”X24” cements slabs on both sides and back filling shall be done by borrowed or excavated earth, with sand cushioning of 25 mm and below and above the cable.  All the materials and labour shall be provided by the Contractor.  The work to be executed shall conform to clauses 2.5 to 2.7 and 2.9 to 2.12.

Peripheral Fencing.

2.15.1 Peripheral fencing shall be provided as per drawing enclosed.

2.15.2 G. I. Barbed wire shall be procured by the contractor.

2.15.3  Rate quoted shall be per running meter of fencing.

2.15.4 The fence posts shall be cast in cement concrete 1:2:4 using 10 to 12 mm HBG  metal, height of RCC intermediate fence posts shall be 2100/2400 mm and height of strut post 2100 mm as shown in the drawing for peripheral fencing.

The fence posts shall not have any honeycombs.  There shall be a minimum cover of 10 mm of cement concrete over reinforcement. The surface of fence posts shall be finished smooth before erection.

The fence posts shall be aligned in excavated pits and concerted with 1:4:8 C.C. containing 40 mm size hand broken granite metal.  The distance between intermediate posts is 3.05 meters.  Corner posts with two struts shall be provided at every 30.5 metres and at all corners.

  - M. S. Gates:

The main gates shall be supplied by the Contractor and erected as per the drawings enclosed.  The main gate shall be supported on RCC pillars.  The rate quoted shall include cost of all construction materials such as metal, sand, bricks, etc. including cost of such gates including their delivery at sub-station site stores.

  - Specifications for the Construction of Control House.

    - General: The specifications for various items of works should conform to the relevant clauses of the APDSS specifications included in the schedules.  The rate quoted shall include cost of all construction materials such as metal, sand, bricks etc. the paras 2.7 to 2.11.16 referred earlier are applicable to the control house construction also.

    - Type of Construction: The building is proposed to be constructed over under reamed pile foundations connected by a plinth beam or on RCC footings. The RCC columns shall be provided over the plinth beam or over RCC footings. The basement shall be in RR Missionary in CM(1:6)  and the superstructure shall be in the brick masonry in CM 1:6, 230 mm thickness.

    - Site Levelling: The site is to be levelled 3 metres all round the building areas including removal of vegetation. The ground also should be raised to the required level if necessary with excavated/borrowed earth as directed by the Engineer.

  - R.C.C. columns and beams

The details of R.C.C. columns and beams to be provided are indicated in the drawings.  The R.C.C. work shall conform to I S 456.

  - Super Structure

The superstructure shall be in brick masonry in cement mortor 1:6 for walls with well-burnt second class bricks.  Rate quoted shall include the cost of all the materials and labour including scaffolding.  The bricks used in all the works under this specification shall have minimum crushing strength of 100 kgs.  Per square centimeter.

  - Filling Foundation and Basement

The work of refilling the foundations and basement is to be done with non expansive excavated soils or sand including watering ramming and consolidating thoroughly in 150 m layers complying to standard specification etc. complete.  Sand when provided shall be at the cost of the contractor.

  - Flooring

The work involves :

Control Room :

- Providing of C.C 1:6:10 with HBG metal 50% of 40 mm size and 50% of 20mm size to a thickness of 100mm including cost and conveyance of all materials all leads and lifts etc.  complete

- Providing flooring with blue double polished cuddapah stones 25mm thick over cement mortor bed of CM 1:8 25 to 40 mm thick inclusive of cost and conveyance of all materials all leads and lifts curing etc., complete for the finished item of work.  Skirting with black polished stone to 150 mm height shall be provided all round the walls inside the control room and office.

2.22	Technical Specifications for Doors and Windows.

2.22.1 The scope of work covered under this specifications is as follows  :

- Supply of M. S. cold formed hallow frames for doors.

- Supply of pre-laminated particleboard flush doors with teak wood lipping.

- Supply of M.S. windows with glass panel doors with 8 mm square horizontal safety bars.

    - Description of the Cold formed M. S. hollow doorframes.

The Cold formed pressed steel frames shall be manufactured from cold rolled sheet metal of 1.25 mm thickness.  The frames shall be free of rust, mill scale, dirt, oil etc.  by mechanical and chemical means before giving an anticorrosive red oxide primer.  The selection of raw materials and construction of frames shall be as per the recommendations of I.S. 513 – 1963 and I.S. 4351 – 1976.

- Material Finish:  The door and frames shall be supplied in red oxide primer painted finish.  Two coats of synthetic enamel paint of approved quality and colour shall be applied after the plastering work is completed.

- Tolerances:  Tolerances on thickness and other dimensions of the materials shall be as per I.S. 513 and I.S. 4351 latest issues.

- Packing : Door frames shall be packed in knockdown conditions ready to be erected at site.  Each frame shall be packed separately along with corresponding accessories in a gunny wrapping. The hallow space shall be filled with CM(1:5) and well cured before erection.

    - Dimensions of the M. S. cold framed Hollow door frames.

The section of the door frame shall be 105 x 60 mm and dimensions as indicated in schedule Bill of section 6.  The thickness of MS sheet used shall be 1.25 mm as per I.S. 4351 1976.  The sizes of the door/windows to be supplied are indicated in the schedule of quantities.

Accessories:  The following accessories shall be supplied along with each door frame.

- Built in (welded) hinges 100mm long 2.5 mm thick – 3 Nos. for single shutter door and 6 Nos. for double shutter door.

- Hold fasts – 6 (six) Nos.

- Bottom tie of 10mm square rod-1 (one) No.

- Fastening bolts and nuts – 8 (eight) Nos.

- Stiffeners – 4 Nos.  on either size and 3 nos. on top at suitable intervals.

The following provisions shall be made in the Door frame  :

- Mortised lock slots.

- All-drop hole

- Tower bolt holes

2.22.4	Shutters: Shutters shall be of 25 mm thick prelaminated particle Board exterior grade (both sides laminated) with 28 mm teak wood lipping all-round.  The rate shall include cost of frames, cost of shutters, cost of fittings, painting the surface in contact with masonry with one coat of solignum paint and painting the teak wood lipping and frame with two coats of best quality synthetic enamel paint over a primer coat (total 3 coats).

    - Sizes of shutters for Doors :  The overall sizes for doors are mentioned in the schedule.  The actual sizes of doors shutters shall be manufactured duly deducting thickness of door frame.

    - Accessories:  The following aluminum accessories shall be supplied along with each Door.

- Tower bolts for double leaf 		3 Nos.

- Tower bolts for single leaf 		2 Nos.

- Aldrops				1 No.

- Stopper for double leaf		2 Nos.

- Stopper for single leaf			1 No.

- Handle					1 No.

    - Windows and Ventilator :  Steel windows and ventilators as per the designs approved by Executive Engineer  conforming to relevant  ISS shall be supplied and fixed in position.  The windows shall be fixed with 4 mm thick white plain glass for control room, with figured glass 4 mm thick of the colour and design approved by the Executive Engineer for others.  The glass shall be fixed by pins and putty etc.  Safety bars of 8 mm MS square rods shall be fixed to the Frame by welding 120mm c/c (horizontally).  The windows and ventilators shall be provided with required MS handles, peg stays and closing arrangement etc.

    - The windows shall be painted with primer of red oxide paint before fixing in position.  The rate shall include all the above items fixed in position for completed work.  The sizes of windows and ventilators shown in the drawing or schedule (bill of quantities) are only tentative. The correct sizes will be furnished by the Executive Engineer during execution. The windows shall be painted with two coats of best quality enamel  paint over a coat of primer(total 3 coats) after completion work.

    - Fixing: It is the responsibility of the contractor of fix the shutters with accessories for the doors and windows.

Note : There may be sometimes lag between supply of the shutters and their fixing to the respective frames.  The contractor shall arrange for fixing of the same on intimation by the Site Engineer.  The bidder shall note the above contingency while quoting the rates in the schedule of materials.  The rate quoted should be for the supply and fixing of doors and windows in full shape.

  - Bed Blocks under Lintels

Rate quoted should be for providing bed blocks in CC 1:3:6 proportion using 20 mm size HBG metal under lintles with necessary form work including cost and conveyance of all materials, all leads and lifts and at all heights and curing etc., for finished item of work.

  - Lintels

The rate quoted should be for RCC 1:2:4 proportion nominal mix for lintels using 12 mm to 20mm size HBG metal including scaffolding, centering, machine mixing, vibrating, curing, finishing, cost and conveyance of all materials, all leads and lifts in all positions of the buildings and at all heights.

  - Sun Shades

RCC 1:2:4 proportion nominal mix for sunshade of 62 mm thick average and 0.61 mm wide using 12 mm to 20 mm size HBG metal including scaffolding, centering, machine mixing, vibrating, curing and finished to the required slopes and providing lip at the bottom ends including cement plastering 12 mm thick CM 1:5 proportion, dubara sponge finish to the exposed faces of sun shades, including the cost and conveyance of all materials

  - RCC Roof Slab

RCC 1:2:4 nominal mix using 12 mm to 20 mm size HBG metal for required thickness as specified in the drawing shall be adopted.  Reinforcement shall be as per clause 2.11 and as per the drawing given by the APSPDCL and cost of steel, binding wire, labour charge for all works pertaining to control room shall be included in item 5 of schedule bill.

  - Plastering Items

i) Plastering to walls is to be done with cement mortar (1:5) proportion 12 mm thick on even surface side and 20 mm thick on uneven surface side including scaffolding, cost and conveyance of all materials, all leads and lifts and curing etc., complete.

ii) Plastering to ceiling shall be done in cement mortar with CM (1:3) 12 mm thick including cost and conveyance of all materials all leads and lifts and curing etc., complete.

  - Painting Items

Costs of tools and plant, paint, brushes etc., required for the work shall be borne by contractor.  The painting work involves.

- Painting 2 coats to the steel work (Grills and frames for windows or ventilators) with synthetic enamel paint first grade of approved make and colour, over a primary coat (total 3 coats) including the cost of the paint and primer.

- Painting the outside of the walls with two coats of cement paint of approved colour and make over a primary coat (total 3 coats) in all heights, including cost and conveyance of all materials, all lead and lifts, scaffolding and curing etc.  Complete.

- Internal walls shall be painted with 2 coats of oil bound distemper of

approved quality over one coat of cement primer paint.  The rate quoted shall include scaffolding, cost and conveyance of all materials, all leads and lifts complete.

The paints used shall conform to relevant IS and samples shall be           submitted and got approved by the Engineer.

2.29.	Drainage, Sanitary and Water Supply Arrangements

A separate toilet with septic tank shall be constructed with necessary water supply and sanitary arrangements.  The porcelain materials such as W.C. wash basins and pillar taps, bib cocks, pit valves etc., are to be supplied by the contractor himself and work executed.  Samples of these materials shall be got approved by Engineer before fixing.  These materials shall conform to relevant IS in all respects and ISS certificates shall be produced at the time of supply

  - Formation of Roads

The roads shall be 5 meters wide with metalled surface and berms on either side.  The cutting or embankment is to be done as per specification for a top width of 10 meters as provided in the schedule to get the road to be formed to even level and required gradient. The payment for cutting earth work and forming embankment providing Hume pipe or construction of CRS masonry for culverts shall be done as per S.No. 44 of Section ‘6’ of this specification and construction of embankment or construction of retaining wall shall be done or the drains/Canals passing abutting to Sub-station site as per S.No. 45 of the Section ‘6’ and road berms will be laid as per the rate provided under excavation / leveling of site.

WBM surface with 150 mm thick metal base using 65 mm metal and gravel 75 mm thick top smooth surface using 40 mm metal and gravel shall be provided and well consolidated with 8 to 10 tonne power rollers as per the schedule items.

3.a.0.	Substation M. S. Structures

3.a.1	General: The main and auxiliary structures required to be fabricated by the successful bidder are R.S. Joists 152 x 152 mm and MS Channel members        100 x 50 mm.  The main structures are fabricated with R.S. Joists 152 x 152 mm.

3.a.2	Drawings: The drawings are to be prepared by the successful bidder and fabrication works taken up.  Two sets of shop drawings are to be handed over to the E.E./ In-charge.

3.a.3	Steel Sections: Steel sections required for these structures like M. S. plate 6 mm etc., are to be procured by the successful bidder.  Firm prices are to be quoted by the bidder.

3.a.4.	Fabrication:  The fabrications of structures shall conform to I.S.  802-1978.  Part-II unless otherwise modified.  All the provisions of I.S. 802 with regard to fabrication shall be strictly adhere to.  Special care shall be taken with regard to straightening, punching of holes and bending of structure members. There should not be any joints for structural supports ,structural members and seating channels.

3.a.5	Inspection

i) Proto types of main structures are to be fabricated and offered for inspection.  Mass fabrication of such structures is to be done after receipt of approval of prototypes.

ii) Mass fabrication of other structures shall be taken up immediately on receipt of contract.

iii) All gauges, templates necessary for conducting tests shall be made available at the time of inspection by APSPDCL Engineer.

3.a.6	Payment for fabrication structures will be made as per sectional weight in accordance with bill of materials.

3.b.	The following equipment shall be erected by the contractor as per the manufacturer’s instruction / and as per the layout / drawings to be furnished by the APSPDCL to the contractor at the time of erection.

- Circuit breakers (vacuum circuit breaker)

- Current transformers

- Potential transformers

- Control and relay panels LTAC PANEL and DC Distribution Board.

- Power transformer 5 MVA / 3.15MVA

- Station transformer

3.b.1.	The scope of work shall include supply, erection and commissioning of Sub-Stations. The contractor will be responsible for the safety of equipment.

3.b.2.	The manufactures’ installation drawings/instructions and recommendations will be furnished to the successful bidder.  The instructions shall be correctly followed in handling, setting, testing and commissioning of all the equipment.  In case of doubt as to the correct interpretation of the manufacturer’s drawings or instructions, necessary clarifications shall be obtained from the Engineer.

The Contractor shall be responsible for the proper erection of the equipment and he will be held responsible for any damage consequent to incorrect handling.

3.b.3	The charges for connecting cables with necessary glands, compounds, lugs, etc., to various equipment’s shall not include under the rates for erection of individual equipment but shall be included under the cable installation.

For erection of control and relay panels LTAC panels and DC Distribution Board in control room the channels required to be embedded in floor and grouting of foundation bolts in these channels, is also to be done by the successful bidder.

3.b.4	11 KV H.G. fuse sets with accessories shall be fabricated as per drawing enclosed.

The 33 KV H.G fuse set shall be fabricated by the contractor after taking necessary approval of the Site Engineer.  All the materials are to be procured by the contractor.

4.  STRINGING OF BUSBAR:

The 33KV and 11KV bus shall be formed with single 200 sq.mm ACSR Conductor respectively and shall be strung to required tension as per the Engineer’s direction. Conductors, Insulators, Bimetallic and other connectors for connection between bus and equipment and between various equipment are to be supplied by the contractor.

The stringing of bus conductors covers installation of insulator strings, post type insulator stack and other accessories, tensioning of conductor, clamping and jumpering to various equipment.

The insulator strings shall be assembled on the ground.  These shall be cleaned, and examined before hoisting.  All the parts including current carrying parts shall be clean without grease, paint and dirt.  Insulators with cracks or chips or those having glazing defects shall not be used.

Damaged conductors shall not be used.  No joints are to be made.  The conductor’s surface shall be clean and smooth without any projections, sharp, cuts or abrasions, etc. and the conductor shall be continuous span.

4.1	Aluminium Clamps: The Alumnium clamps of various sizes and type for 33 KV: 11 KV Bus shall be supplied by the contractor.

- EARTHING SYSTEM :

The earth mat shall be laid as per the approved layout, to be furnished to the contractor at the time of award of the contract.  The earth mat shall be formed with the steel flats burried in the ground at a depth of 500 mm.  (Size of the trench for laying the earth mat shall be of 300 mm x 500 mm).

The earth mat shall extend over the entire switchyard as per the layout the be furnished to the successful bidder.

While forming the earth mat all the junctions of the steel flats and risers taken from the earth mat for giving earth connections to equipment, steel structures, conduits, cable Sheaths etc. shall be properly welded.

Provisions shall be made for thermal expansion of the steel flats by giving smooth circular bends.  Bendings shall not cause any fatigue in the materials.

The earth mat shall be formed by 75 x 8 mm steel flat.  After the completion of earth mat, the earth resistvity may be measured.  In case the earth resistance is more than two ohms, earth mat maybe extended and extra electrodes installed so that the earth resistance is less than two ohms.

All paints, enamel and scale shall be removed from surface of contact in metal surface before making ground connection.

The risers taken along with main switchyard structures and equipment structures (upto their top) shall be clamped to the structures at an interval of not more than one metre.

Grounding electrodes of 75 mm dia 2.75 m long C.I. pipes shall be provided as per the drawing.  Their tops shall be welded to a clamp and the clamp together with the electrode shall be welded to the ground mat.

Lightning arrestors shall be provided with earth pits near them for earthing (as per the standard practice).  Cast iron pipes 75 mm in dia and 2.75 metres long and 9.5 mm thick shall buried vertically in the pits and finely broken coke shall be filled at-least 150 mm around pipe for the entire depth.  Where it is not possible to go to a depth of 2.75 metres, 1.3 x 1.3 metres MS plates 25 mm thick shall be buried vertically in pits of 2 metres depth and surrounded by finely broken coke at-least 2 metres away from any building or structure foundation.  The plates shall be at-least 15 metres away from any building or structure foundation and shall be at-least 15 metres apart.  These earth pits in turn shall be connected to the earth mat by MS flat 75 x 8 mm.  The joints and tap offs, when welding is done, shall be given a coat of bituman paint and covered with Hession tape to avoid rusting, rate quoted for earthing shall include the cost of B.H. coke, the cost of excavation for earth pits and cost of bitumen paint for the joints.

5.1	Pipe Earthing materials: The pipe earthing material to be supplied by bidder shall conform to relevant IS.  The pipe shall be cast iron 75 mm dia and length 2750 mm shall be supplied along with 16 mm dia M. S. bolts, nuts and washers.

- CONTROL CABLES.

7.   LAYING OF CABLES:

This section covers laying of cables in cable ducts ,cable joining.&  termination at both ends and testing of the complete cable installation.  The rate of cable installation.  The rate of cable laying shall be including cost of cables.

The L.T. Control cable shall be copper cables and the LT Power cable shall be Aluminum cables.

7 (a)	Copper cables shall comprise of copper wire of 2.5 sq.mm cross sectional area and number of wire being 2,4,10 as the case may be.  The rate for cable termination shall include cost of ferrules, lugs and labour charges of the same.

7 (b)	The aluminum LT Power cables shall be of the size 3 ½ core 95 sq. mm, 3-1/2 core 25 sq. mm and two core 4 sq. mm and the above cables shall be used for station transformer to LT AC panel, from LT AC panel to yard lighting junction Box and battery charges, and from yard lighting justing to Flourescent lamps respectively.

The cable schedules will be furnished to the contractor.  The cable laying shall be done strictly in accordance with these schedules.  There shall be no joints in between point to point termination of the above cable.

All the electric equipment is to be set in place and aligned.  The contractor shall provide power and auxiliary connection to the equipment and shall work in cooperation with Contractors representatives in obtaining correct direction of rotation and commissioning of the equipment, cable laying shall also include termination of cables i.e. both ends of cable of equipment switch-gear, control and protection panels etc.  as well as equipment to marshalling boxes and marshalling boxes to switch-gear panels.

Secondary terminal of CTs/PTsSS shall be connected to marshalling boxes through cables and then further connected up by cable panels or other equipment.

Cables lugs shall be provided by the contractor and the costs of lugs shall be included in the quoted rates for cable laying.  Contractor shall supply all other cable terminating accessories, like jointing ferrules, cable clamps, cable grips, cable compound flux, tapes, etc., as necessary and shall include supply of accessories in the quoted rates for cable laying.  Dressing / bunching of all individual cores of the cable shall be done in a neat fashion.  The contractor shall drill holes suitable for the cables in cable gland plate whenever necessary

Cable lugs be compressed on the conductor ends by means of suitable insulating sleeves shall be furnished and covered over the bare ends of the connections so as to prevent accidental contact with the grounds of with the adjacent terminals.

The insulating sleeves shall be fire resistant, and long enough to over pass the conductor installation and shall be of correct size of the conductor used.

Cables: entering the control room from outdoor areas shall be sealed.

Standard cable grips and seals shall be utilised for cable pulling.  After pulling a cable, the contractor shall attach Aluminium cable markers at both ends of the cables and at the control room entry.  The cable number and other data shall be punched and the cable markers are securely attached to the cables.  Cable shall not be jointed.  When absolutely necessary, the approval of the APSPDCL Engineer at site should be taken before resorting to jointing.  Sharp bending and kinking of cables shall be avoided.  Cables shall cross control room basement wall in 100 mm dia A.C. pipe embedded in cement concrete basement wall.  These pipes shall be supplied and installed by contractor.  The cost of these pipes shall be included in the rate to be quoted against item 7 of section 6 of this specification.

In each cable run some extra length as per the direction of the Engineer shall be kept at a suitable point adequate for two straight through joints at the cable terminal pits where the conductor and cable insulation will be terminated.

Before any cable terminal connections are made, conductor’s insulation shall be pulled out at the end and identifying ferrules shall be fixed according to the wiring diagrams.  Connections shall be made according to the wiring diagrams to be supplied by the APSPDCL .

Polarity or phasing shall be checked before connections are made and corrections of polarity, phasing or rotation shall be made by the contractor without additional cost.

Control cable terminations shall be made in accordance with wiring diagram using colour codes established by the APSPDCL for the various control circuits, by code marked wiring diagrams furnished to the contractor for this purpose or any other approved means of identification.  It is the intent that the contractor shall terminate the cable, which he installs.

Additional work of testing and reconnecting where leads have been brought by the contractor to the terminal Boards and connected, but where on further testing, reversed or other rearrangement of lead turns out to be necessary, shall be performed by the contractor without additional cost.

Jointing of cables shall be in accordance with Indian Standard codes.  The manufacturer’s special instructions on materials and tools required for cable jointing work shall be arranged by the contractor.

Metal sheath and armour of the cable shall be connected to the earthing system of the station by a steel strip wire.  Bending the metal sheaths of single core cables in close trefoil formation shall be as stipulated in the relevant codes of practices.

The contractor shall furnish two sets of cable layout drawings after installation, indicating altered cable routes and location of straight joints.  Details of alternative sizes of cables used if any shall also be furnished in such drawings.

- L.T AC SUPPLY PANEL

8.1.	The A.C. Panel with all accessories shall be mounted in a metal sheet steel, abide for indoor, floor mounting free standing type with following features: -

a)	Made of cold rolled sheet steel of thickness not less than 3 mm.

- It shall be completely dust and vermin proof and all the doors shall be hinged type with suitable gaskets for the mating surfaces, in-comer, and all the feeders shall be provided with hinged doors individually.

- Provision of glands for incoming and out going cables, suitable lugs for the terminators.

- Shall be painted with 2 coats of the battle grey paint, over a coat of primer.

8.2.	Incoming supply from Station Transformer: It shall be provided with 3 pole             N switch fuse unit 100 Amps with the following:

i)	Volt meter (0-500 V)

ii)	Ammeter (0-100 A)

iii)	Selector switches for Voltmeter and Ammeter

iv)	ON/OF-RED/Green and R.Y. B Supply indication lamps.

8.3.	Bus bar (100 A) shall be made of high conductivity Aluminum alloy of electrical grade conforming to IS 5802.

8.3.1	The Bus bar shall be insulated throughout their lengths by heat shrunk PVC sleeves.  The PVC Sleeves used shall be able to withstand the temperature attained by the Bus bars during normal/short circuit conditions.  The bus bar shall be identified with coloured bonds to identify buses.

8.4.	Out Going Feeders

8.4.1	32A - 3 Nos. with switch fuse units.

8.4.2	16A – 3 Nos.  with switch fuse units.

NOTE:  (1) All switch fuse units shall conform to IS4064 Part – 1 1978 and of reputed make.

(2) All the connections inside the panel shall be with PVC insulated copper wire of adequate size.

9. D . C.  Annunciation Board

9.1.1	The D.C. annunciation board shall be of 1400 MM X 900 MM X 12 MM hylem sheet with grey colour decolam top.  The lining of the Board shall be of Aluminium angle size 15 mm X 15 mm X 4 mm and shall have the following features, and shall be mounted on M.S. angle stand.

9.1.2	AUXILIARY SUPPLY : The following auxiliary supplies shall be available.

(a) 230 V  2 Wire 50 Hz AC for panel lighting.

(b) 24V 2 wire D.C. Supply for control and alarm circuits with an earthed G.I. wire run all along the cable.

9.1.3	Engraving of single line diagram of the 33/11 KV Sub-station with identification for power transformer, feeder breakers P.T.s and C.T. s with ratings.

9.2.	Providing of OLTC and Transformers buchholzs alarm circuits and alarm acceptance switch for power transformer with indication.

9.3.	Providing of tripping circuit to trip of 33 KV Group control circuit breaker in case of bucholtz trip contact operation.

9.4.	Wiring :  All the wiring inside the panel shall be done with multistrand copper wire of adequate size with necessary terminal blocks for 2 circuits (power transformer and feeder breakers).

10.  ALUMINIUM POWER CABLES  :

They shallbe 650/1 100V grade heavy duty PVC/PVC insulated and sheathed, stranded aluminium conductor cables conforming to relevant IS.

All the cables other than  4 sq.mm are armoured.

- ILLUMINATION OF SWITCHYARD :

The equipment such as lighting distribution Boards, lightin panel for lighting, lighting fixtures, fuminaries, lamps, wiring accessories, junction boxes conduit accessories, fitting etc.  and materials as would be found necessary for illuminating the switchyard along with 125 watts MV lamp, are to be supplied by the contractor.  The contractor also has to arranged conduits, conduit accessories required for the work and cost of all materials, labour shall be included in the scope of the work to be done by the contractor.

The lighting system shall consist of normal AC lighting from 3 phase 415 Volts supply (AC supply panel).

It is proposed to provide 125 watts MV lamp for AC lighting as per lighting arrangement to be furnished.  The locations of the light fittings in the switchyard will be indicated by the Site Engineer.

    - SUPPORT FOR  FIXTURES

i)  The lights shall be mounted on separate 8 Mts. PSCC Poles with necessary cantilever arrangement for which required materials has to be procured by the contractor. All the accessories, G.I. pipes, clamps, etc., required for mounting the fixtures shall be supplied by the contractor.  The cantilever arrangement for fixing lighting fixture shall comprise of M.S. ‘U’ clamps fabricated from M.S. Channel 100 x 50 mm and G.I. pipe of 40 mm dia. The unit rate for fixing the luminaries shall include cost of above material and labour.  For AC lighting the mounting arrangement shall be earthed at two locations with 8 SWG G.I. Wire to be supplied by the contractor.

ii) All lighting fixtures shall be mounted in accordance with standard installation practice.

iii) All lighting fixtures shall be assembled, installed and wired Splices in lighting circuits shall be avoided. Required size of fuses shall be provided for each lighting fixture in the junction box.  After completing the connections to all outlets the contractor shall check up all portions of the lighting system to ensure satisfactory operation.

11.A. 	ELECTRIFICATION OF CONTROL HOUSE

Drawing showing the electrification of control house will be furnished  with the contract.  Wiring work is to be done with PVC unsheathed aluminium cable in surface PVC conduit.  SwitchBoards are to be provided  at the appropriate palaces atleast one in each room as directed by the APSPDCL Engineer.  All light and  fan controls for the points emanating from each Switch –Boards are to be provided at one place on a suitable size teak wood board covered with decolam sheet

The work should be carried out in conformity with the code of practice for electrical wiring and fittings in Government buildings and the Indian Standard Specification.  Samples of fittings, switches and all other materials being used in the work must be got approved by the Executive Engineer before commencement of the work.  Holes made in the walls for fixing fittings and for taking mains are to be closed with cement mortor and neatly finished and white wash done by the contractor.  The makes of all the materials proposed for use in the work must be furnished with the bid.

PVC conduits of 50, 40, 25 and 20 mm diameters as stated in schedule are to be fixed in walls and roof slab by making necessary grooves by concealing – GI wire is to be left over in conduit pipes to draw electrical wires at a later date.  The rate shall include cost of pipes, Junction Boxes, GI wire earthwire, earth clips (copper) and other materials and labour charges.  All materials used shall have IS certification.

Ceiling fans with regulators required will be supplied by the contractor.

11A.(I)	FIRE EXTINGUISHERS  :

The 6.8Kg Co2 Fire extinguishers to be supplied and erected shall be of trolley type complete with 1st filling horn & house complete, confirming to IS 287.

Statutory test certificates issued by the Chief Controller of Explosives department & Cylinder Manufacturing Test Certificates shall be furnished along with the fire extinguishers to be supplied and erected.

11.A.(II)BOLTS & NUTS :

The make of Bolts & Nuts shall be GKW or equivalent. Test certificates for bolts & Nuts shall be submitted..

11.A.(III)G.I. BARBED WIRE  :

The GI Barbed wire to be strung peripheral fencing shall be glidden type – conforming to IS – 278 (with latest amendment) with line and point wire of 2.5 mm dia.

12.  ERECTION, CABLE LAYING, EARTHING, SWITCH YARD ILLUMINATION ETC.

  - General:

The erection of structure and equipments, cable laying and earthing has to be done by the contractor using his own T & P, a list of materials / equipment that will be required for erection are to be procured by the contractor.

12.2	SAFETY: The contractor shall provide and make all necessary arrangements for the safety of the staff and labourers, at site of work.  The APSPDCL  will not in any way be resonsible for any accident, minor or fatal to any person at the site of works or for any damages arising therefrom during erection and this shall be the contractor’s responsibility.  The staff insurance charges, if any, shall be borne by the contractor himself.

12.3	ERECTION OF STRUCTURES:  The structures shall be erected by piecemeal method on the foundation, after allowing the required curing time for the foundations.  The members shall not be strained or bent during the course of erection.  Care shall be taken to see that the jointing surfaces are clean and free from dirt or grit and fit properly.  The structures shall be erected strictly in accordance with the approved drawings.

The bolts and nuts, spring washers and pack washers required for the work will be supplied by the contractor.

After erection of structures the bolts shall be checked to ascertain that all nuts are fully  tight.  The contractor shall ensure that all the bolts are in position and fully tightened.

The structure must be truly vertical after erection and no straining will be permitted to bring them to vertical position.

13.  FINAL CHECKING, TESTING AND COMMISSIONING

FINAL CHECKING : After completing the works, the contractor shall ensure that following points are not missed :

- Backfilling is completely done and compacted along with leveling.

- Coping / Muffing / Plinth surfaces are done to proper shape.

- Bolts of the structures are properly tightened.

- Cables are properly dressed.

- Equipment such as breakers, isolators are properly operation.

13.1	TESTING  : The contractor shall give necessary assistance to the APSPDCL  Engineers at the time of testing the equipment by providing required labour and testing equipment at the test location.  Any defects found during testing shall be rectified by the contractor forthwith.  Without any charges to the Board.

13.2	COMMISSIONING : All the tests shall be completed by the contractor successfully before commissioning of Sub-Station.

14.  RECTIFICATION OF DEFECTS DURING THE DEFECTS LIABILITY PERIOD:

The defects liability period of the Sub-Station is 12 months from the day of commissioning and acceptance by the APSPDCL. Defects if any, noticed during the above period shall be rectified by the contractor free of cost of the Board on hearing from the APSPDCL.

15.  SECURITY  FENCING

  - Security fencing shall be laid to the height of 1Mtr above the retaining wall of the switch yard.

  - The fencing post shall be M.S. angle (2X65X65X6) of 1.5 Mts in length welded back to back from T section. The corner post shall be 150X150 mm RS joists of 1.5 Mts. length.

  - Fencing wire shall be the mesh of squire shaped secling 50X50 mm with GI wire of 3 mm dia meter and shall be welded on the frame 3 Mts X 1 Mtr X 6 mm made of 50X6 mm M.S. flat.

  - All the fencing posts shall be mass concreted in the retaining wall itself with a span of 3 Mts.

  - All the fencing poles shall be painted with two coats of red paint over one coat of primer.

Note: The Contractor has to follow REC standard for the work where ever it is not specifically mentioned above.

TECHNICAL SPECIFICATION

FOR 24V 40 AH SEALED MAINTENANCE FREE LEAD ACID WITH BATTERYCHARGERS

  - SCOPE : This specification covers the design, manufacture, testing before despatch supply and delivery of 24V, 40 AH Sealed maintenance free lead acid batteries with chargers suitable for indoor application (with rack)/out door application.

The Batteries with trickle charger units are intended to be used for operating 33 KV,     11 KV SF6/Vac. Circuit Breakers with auto reclosing feature. The rating of closing and opening coils is 400 watts (operating time is 100 ms) and the rated operating sequence is 3 Min Co-3 Min. – Co or 0-0.3 Sec. Co-3 Min-Co.

The Batteries should have a capacity sufficient to operate 2 Nos (in case of 24V) 11 KV Vac./SF6 Circuit Breakers simultaneously for about 25 closing operations on each when used without a charger.

- STANDARDS :

i) IS 1885 (Part VIII)	   :	Electro Technical Secondary cells and batteries

ii) IS 1651-1991	  :        Stationery Cells & Batteries Lead Acid battery with

tubular positive plates.

iii) ID 8320 – 1982       :	Sulphuric Acid General requirements and                  methods

of tests for Lead acid storage batteries.

iv) IS 1069/1964	  :	Water for storage batteries.

Materials meeting any other equivalent International standards which ensures equal or better quality than the standards mentioned will be acceptable. In such cases the copy of the standards (English version) adopted should be enclosed to the tender.

- CLIMATE CONDITIONS : The climate conditions under which the equipment shall operate satisfactorily are as indicated in page (3) of General and Financial terms and conditions for supply of materials.

4.	RATINGS :

4.1.	Battery		:	24 V

4.1.1.	Type			:	Sealed and maintenance

Free Lead Acid Battery

4.1.2.	Nominal Voltage	:	2.0 V

of the complete Bank.

4.1.3.	Voltage/Cell		:	2.0 V

(The cell voltage shall not exceed 2.25 with a continuous low rate floating charge and shall not be less than 1.75 V at the end of the emergency discharge).

    - Capacity of 			40 AH

Batteries

(In Amp.hours at

10 Hour rate to an end voltage of 1.75 V

per cell).

  - BATTERY CHARGER :

4.2.1.Type		:	Constant voltage and current limiting charger

4.2.2. Input voltage	:	415 V, 50 Hz, 3 PH/240V, 50 Hz, 1PH shall work 				satisfactorily for voltage range of – 30% to +10% with 			a frequency variation + or – 5%.

4.2.3. Charger Output		:

4.2.3.1. Float Voltage		:	27 V + or –  5%

4.2.3.2. Boost Voltage	:	29 V + or – 5% (max)

4.2.3.3. Regulation		:	+ or – 1%

4.2.3.4. Charger current	:	5A

4.2.3.5. Ripple			:	< 2% rms

4.2.3.6. Efficiency		:	Not less than 75% at full rated load.

4.2.3.7. Current Limit		:	105% of rated load

4.2.4.    Insulation		:	Not less than 5 mega ohms.

In any of the following cases

- Between DC output terminals and AC input terminals.

- Between AC input terminals and earth.

- GENERAL REQUIREMENTS :

  - BATTERY :

The Batteries required under this specification are for supplying aux.D.C. supply to control circuits of circuit breakers. The battery shall be capable of withstanding large discharge currents for operating 33 KV & 11 KV SF6/Vac. Circuit Breakers. It shall be of rugged construction designed for long life and for working satisfactorily under the severest operating conditions and shall conform to the relevant Indian/International standard of latest issue. The battery shall be supplied complete with all required accessories for their efficient operations and such parts/accessories shall be deemed to be within the scope of this specification. Whether specifically mentioned or not.

The rating of the Batteries is specified at 27 Deg. C. However, the battery shall be capable of operating satisfactorily in outdoor applications when it is housed in a Cubicle between 5 deg. C and 50 deg. C (at reduced capacities) and in locations where the relative humidity varies between 12% and 100%.

All parts particularly removable ones shall be interchangeable with each other.

The separators shall be micro porous absorbent glass material with high porosity. All connectors shall be of lead plated copper. All inter cell and nuts and bolts shall be of brass and lead plated. The lead plating shall be adequate and tenacious. The cells shall be suitably marked as per I.S.S.

The D.C. Battery shall be operated without intentional ground.

  - BATTERY CHARGER (FLOAT CUM BOOST)

The battery shall be offered with suitable charger requiring low maintenance. The charger shall be of full wave semi controlled thyrister bridge rectifier type with automatic voltage regulator unit and with necessary printed circuit boards, transformer and relays etc. The charger shall be provided with a regulator to facilitate controlling of the cell voltage and to stabilize the output voltage within + or – 1% of the set D.C. value, for AC mains supply voltage variation of + 10% or –30% and frequency variation of + or – 5% and D.C. load variation of 0-100% and also when all the three variations occur simultaneously. The charger shall be provided with an automatic current limiting facility such that when charger output current exceeds 10% above the rated current, the charger voltage should be brought down automatically so that the charger output current does not exceed the set value. Spike suppressors (preferably on both primary & secondary side) and surge arresters are to be provided. Peak inverse voltage of all thyristors/diodes shall be rated for minimum of 600V. screening circuit to be incorporated for reducing transfer surges.

A manual and automatic changeover arrangement from quick to trickle and vice versa shall be provided. Provision should be made to vary the charging current of Trickle/high charge in manual mode also. In the event of A.C. supply failure, when the battery is on boost charge, the available battery capacity shall be automatically connected to the DC load.

The charger should include AC ON/OFF switch preferably MCB of suitable capacity, fuse protection for AC and DC, battery reverse polarity protection, with “Power On” “Charger On”, Boost Charge” lamp indications. A bell to be provided for giving alarm with indication in case of AC supply failure/charging failure. The equipment shall also include a moving coil voltmeter of suitable size and range which shall indicate voltage on pressing a test push button, a dual range moving coil ammeter (with centre zero) to show quick/trickle charging currents and discharge current of battery. The indicating instruments shall be of flush mounting type with dust tight covers. The instruments shall be approximately 60/70 mm square with 270 Degree scale or alternatively 60/70 mm square with 90 degree scale. Dial shall be white with black numbers and lettering. The make of the ammeters, voltmeters to be provided should be got approved before supply. The charger shall have suitable indicators to visually know its mode of operation.

The battery charging equipment shall be complete with all parts that are necessary for their efficient operation. Such parts shall be deemed to be within the scope of this specification whether specifically mentioned or not.

The internal wiring of the charger shall be carried out with PVC insulated 650V grade standard copper conductor. The control wiring shall be carried out with 2.5sq.mm copper conductor. All wiring for external connections shall be brought to 650V grade single piece mounted terminal blocks with barriers. Suitable vertical terminable blocks shall be provided. Terminal connectors provided for wiring shall be stud type and not screw type.

The D.C. output shall be terminated in the terminals, with facility to receive the battery wires and the load cable, with similar arrangements for A.C. input terminals for receiving A.C. wiring cable.

All the external cables to be connected to the charger shall be arranged for bottom/side entry with proper cable glands.

All the important component of the charger must be easily accessible for maintenance, repair, replacement in case of trouble without giving interruption to the total D.C. supply as far as possible.

5.3.1. System Box (For 24 V Battery and Charger)

The 24V Battery and charger shall be housed in self supporting outdoor cubicle designed with good ventilation to cool the components so as to take care of the temperature effects. The units will be located in OUTDOOR YARD by the side of vacuum circuit breaker which are mounted on a suitable angular or tabular structure.

The cubicle housing trickle charger along with electrical instruments/components in the upper compartment and the battery in the lower compartment shall be completely weather proof & vermin proof. A suitable hood shall be provided to protect the equipment from rain.

The cubicle shall be made of suitable M.S. angles and sheets of not less than 16 SWG to with stand the weight of charger and battery cells and shall be of robust constructions.

The door covering the entire unit shall be provided in the front, facilitating reading of instruments inspection/service and maintenance of battery cells and charger components periodically. The door shall be fixed using screws so as to observe all meter readings and indications without opening the door through a perspect sheet.

Suitable provision shall be made for the escape of fumes emanating from the cells and heat from changer components.

Suitable anti Corrosive, acid resistive paint is to be provided to interior side of the box.

5.4.	1 No. cell testing centre zero volt. Meter with suitable range shall form part of the supply.

- TESTS & TEST CERTIFICATES :

The batteries are to be tested as per relevant I.S. and the type test certificates are to be furnished for approval. End cell voltage shall be as per relevant I.S. The trickle charger is to be tested for its rating and the test certificates are to be furnished for approval. A copy of the test certificates issued by any National Laboratory shall accompany the tender.

- DRAWING & LITERATURE :

Detailed Drawings, Circuit details and technical literature of batteries and trickle chargers shall be enclosed to the offer. Tenders not accompanied by the above are liable for rejections. 2 copies of these drawings circuit details and literature are to be supplied along with each unit in the event of order. Trouble shooting charts shall be supplied with each unit to trace faults in the charger with voltage and resistances to be measured at various test joists.

- PAINTING :

Before painting, all ungalvanised parts shall be completely cleaned and made free from rust, scale and grease and all external rough surface cavities and casting shall be filled by metal deposition. The interior parts and internal structural steel work shall be cleaned of all scale and rust by sand blasting or other approved method. All external surfaces shall receive a minimum of 3 coats of paint. Anticorrosive/Acid resistant is to be provided for interior side of the system box. The paint shall be guaranteed for 5 years from the date of receipt of material.

- INSPECTION :

  - All routine tests and inspection shall be made at the place of manufacturer unless otherwise especially agreed upon by the manufacturer and purchaser at the time of purchase. The manufacturer shall afford the inspector representing the purchaser all reasonable facilities, without charge to satisfy him that the material is being furnished in accordance with this specification.

  - The purchaser has the right to have the tests carried out at suppliers cost by an independent agency wherever there is a dispute regarding the quality of supply.

- PACKING :

The equipment shall be delivered suitably packed. Although the method of packing is left to the discretion of the manufacturer, it should be robust for rough handling, that is occasioned during transportation by rail/road.

11.	GUARANTEED TECHNICAL PARTICULARS : The guaranteed technical particulars shall be furnished by the bidder as in Annexure I.

ANNEXURE – I

GUARANTEED TECHNICAL PARTICULARS

| 1. | Type of Designation as per I.S.S. | : |  |
| --- | --- | --- | --- |
| 2. | Manufacturer’s type designation | : |  |
| 3. | Amphere hour capacity at 10 Hrs. rate of discharge to 1.75 V | : |  |
| 4. | Total No. of plates per cell | : |  |
| 5. | Nominal cell voltage (volts) | : |  |
| 6. | No. of Cells in each bank | : |  |
| 7. | No. of spare cells if any in each bank | : |  |
| 8. | Internal resistance for each cell (micro ohms) | : |  |
| 9. | Resistance of the battery including inter-connection between the cells (ohms) | : |  |
| 10. | Cell discharge rate in Amperes (from rated voltage to final discharge voltage) | : |  |
| i) | 5 Hrs. Discharge rate in Amp. | : |  |
| ii) | 2 Hrs. Discharge rate in Amp. | : |  |
| iii) | 1 Hrs. Discharge rate in Amp. | : |  |
| iv) | 30 Min. Discharge rate in Amp. | : |  |
| v) | 10 Min. Discharge rate in Amp. | : |  |
| vi) | 1 Min. Discharge rate in Amp. | : |  |
| vii) | 30 Sec. Discharge rate in Amp. | : |  |
| viii) | 1 Sec. Discharge rate in Amp. | : |  |
| (Please furnish a graph showing Amps. Against time for the type of Battery offered). |  |  |  |
| 11. | Short circuit current (Amps) |  |  |
| 12. | i) Material of cell containers | : |  |
|  | ii) Material used for battery box | : |  |
| 13. | Thickness, type and materials of separators | : |  |
| 14. | Constructional details and dimensions |  |  |
|  | i) Positive plate | : |  |
|  | ii) Negative Plate | : |  |
|  | iii) Surface area of plates sq.mm. | : |  |
| 15. | i) Ampere hour efficiency % | : |  |
|  | ii) Watt hour efficiency % | : |  |
| 16. | i) Recommended float charge current and voltage | : |  |
|  | ii) Recommended boost charge current and voltage | : |  |
| 17. | Time required for boost charging from discharged condition |  |  |
| 18. | i) Max. charging current/Cell | : |  |
|  | ii) Nominal charging rate | : |  |
| 19. | i) Whether explosion provisions or vent plugs provided | : |  |
|  | ii) Whether vent is spill proof | : |  |
| 20. | Type of intercell connection and whether they are covered with plastic sleeves. |  |  |
| 21. | i) Dimensions of each 12 V Block/Cell : |  |  |
|  | Length mm | : |  |
|  | Width mm | : |  |
|  | Height mm | : |  |
|  | Thickness of container mm | : |  |
|  | ii) Nett weight of the cell complete with acid 12 V Block (Kg) |  |  |
| 22. | Expected life span of battery | : |  |
| 23. | Accessories provided | : |  |
| 24. | Special conditions if any | : |  |
| #### B) CHARGER |  |  |  |
| 1. | i) Charger Type | : |  |
|  | ii) Type of rectifier | : |  |
| 2. | No. of Units | : |  |
| 3. | Manufacturers type Designation | : |  |
| 4. | A.C. Supply | : |  |
| 5. | Rated D.C. Output (KW) | : |  |
| 6. | Rated D.C. Output voltage (Voltage) | : |  |
| 7. | Rated D.c. Output current (Amps) | : |  |
| 8. | D.C. Output voltage regulation from No load to full load (volts) | : |  |
| 9. | Maximum ripple current | : |  |
| 10. | Changeover from boost to trickle (Automatic/Manual) | : |  |
| 11. | Protection over voltage, under voltage protection reverse polarity protection etc., provided. | : |  |
| 12. | Maximum permissible temperature rise over an ambient temperature of 50 degree C. |  |  |
| 13. | Overall efficiency | : |  |
| 14. | Load limiting feature | : |  |
| 15. | Unit Dimensions | : |  |
|  | i) Width ii) Height iii) Depth | : : : |  |
| 16. | Unit shipping weight | : |  |
| 17. | Recommended spares | : |  |
| C) SYSTEM BOX/RACK :- |  |  |  |
| i) | SYSTEM BOX |  |  |
|  | a) Dimension of Box b) Weight of box c) Gauge of Material d) painting details |  |  |
| ii) | RACK |  |  |
|  | a) Dimension & Weight | : |  |
|  | b) Description | : |  |
|  | c) Material | : |  |
| #### D) DISTRIBUTION BOARD |  |  |  |
|  | a) Double pole Rotary Switch for incoming D.C. Supply | : |  |
|  | b) HRC fuses for the above | : |  |
|  | c) Double pole 10 A ON/OFF Rotary switches | : |  |
|  | d) HRC Fuses for the above | : |  |

- ERECTION OF BAYS:

  - Foundations:

    - The Cement Concrete used for the foundations shall be M-150. The sand used shall be composed of hard silicon material and well sieved. It shall be clear of a sharp angular grill type and free of earthly organic matter and salts. The aggregate shall be clean broken hard granite. It shall be as far as possible cube like, preferably angular, but not flanky, preferably clean and free from earth organics. 38mm aggregate shall be of size.

    - Water used for mixing concrete shall be fresh, clean and free from oils, acids, alkali water shall not be used.

    - Proper moulds adequately braced to retain proper shape while concreting shall be used. The mould shall be made water tight so that cement cream will not come out leaving only sand and jelly,consequently forming honey-combing in the concrete.

    - After concreting, top surface shall be finished smooth. Plastering of outer surfaces shall be done with 12mm thick with 1:3 cement mortar. White washing with white cement shall be done neatly.

  - Fabrication

    - All pieces shall be straight, straightening shall not damage the material. Hammering shall not be permitted for straightening and/or flattening of members. Sharp bends are not permitted. Cutting may be effected by shearing, cropping, flame cutting or sawing. The surfaces so cut shall be clean, smooth reasonably square and free from distortion.

Holes in the members shall either be drilled or punched and shall not be formed by flame cutting process.All blurrs left by punching or drilling shall be completely removed.

It shall be ensured that fasteners provide positive attachment at all times and under conditions when the structure is subject to vibrating loads. Bolts used for erection shall preferably be of 12,16,20mm diameter and in no case bolt diameter shall be less than 12mm. The length of the bolt shall be such that the threaded portion does not lie in the plane of contact of members.

It shall be ensured that the threaded portion of the bolt protrudes not less than 3mm and not more than 8mm over the nut after it is fully tightened. Holes shall be cylindrical and perpendicular to the structural members. Oval or lobed forms of holes shall not be permitted. The diameter of holes shall be equal to the diameter of the bolt plus 1.5mm. The accuracy of the location of the holes such that for any group of members where assembled, the holes shall admit the bolt at right.

| Spacing of Bolts and Edge distances: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Bolt dia (mm) | Hole dia (mm) | Bolt spacing (mm) | Edge hole center to rolled (mm) | Distance min. hole centre to sheared or flame cut edge (mm) |
| 12 | 13.5 | 32 | 16 | 20 |
| 16 | 17.5 | 40 | 20 | 23 |
| 18 | 21.5 | 48 | 25 | 28 |

| Spring washers of positive lock type of the following thickness shall be provided for insertion under all nuts. |  |
| --- | --- |
| Bolt dia (mm) | Thickness of spring washer (mm) |
| 12 | 2.5 |
| 16 | 3.5 |
| 18 | 4 |

1.2.2	Bolts and nuts:	Nominal nut size		Proof stress (N/sq.mm)

M16				 490

M20				 500

1.2.3	The bolts and nuts shall be hot dip galvanised as per IS-1367

    - Spring washers shall be of type B and shall confirm IS-3063. The spring washers shall be made from high quality spring steel conforming to IS-4072. The spring washers shall be electrogalvanized with a coating thickness of 25 microns.

    - The structures shall be erected piece-meal method on foundations after allowing the required curing time for the foundations. After erection of structures, the bolts shall be checked to ascertain that all nuts are fully tight shall lensure that none of the bolts are leftout. The structure shall be truly vertical after erection and no stringing is premitted to bring them to vertical position. The tolerance allowed for verticality is one in 360 structure height.

1.3	Stringing of Bus bar: 33KV and 11KV bus in 33/11KV Sub-Station shall be formed with panther conductor (200 Sq.mm	AAAC) to a tension of 250Kg comprising of three phases. The bimetallic clamps and other connectors required for connections between bus and equipment and between equipments are to be procured by contractor. The stringing of bus conductors covers hosting of tension insulator strings, suspension insulator strings, post type insulator stacks and other accessions along with tensioning of conductor and clamping. The jumpering to the equipment shall be arranged properly.

The insulator strings shall be assembled on the ground. These shall be cleaned and examined before hosting. All the parts including curent carrying parts shall be clean and smooth without greese, paint, and dirt. Insulators with cracks or chips or those having glazing defects exceeding 0.5 Sq.mm shall not be used.

The sag of bus conductor shall not be more than 1%. Damaged conductor shall not be used. No joints are to be made. The conductor surface shall be clean and smooth without projections, sharp points, cuts, or abrasions etc. and the conductor shall be continuous in line span.

1.4 	Earthing:  The earth mat shall be as per the approved layout. The earth mat shall be formed with steel flats buried in the ground at a depth of 500mm. All the junctions of steel flats while forming earth mat and taking raisers from earthmat for giving earth. Connections to equipments shall be properly welded. All joints shall be provided with suitable angle pieces for contact between two flats. Provision shall be made for thermal expansion of steel flats by giving smooth circular bends. Bending shall not be cause any fatigue in the material of bends.

Earth mat shall be formed by welding 50X6mm flat. After completion of earth mat, earth resistivity shall be measured. In case, earth reisistivity is more than one ohm, earth mat shall be extended, extra electrodes shall be installed so that earth resistance is less than one ohm.

The joints and tap offs when welding is done shall be given a coat of Bitumen paint and then covered width Hessain tape to avoid rusting.

1.5	Cabling: Cables shall be 2.5Sq.mm Copper with cores 4 and 10. Cable laying include termination of cables is at both ends of cable of equipment, control and protection panels etc. as well as equipment to marshalling boxes to switch gear panels. Cable lugs, cable terminating accessories like jointing ferules, cable clamps, cable grips, cable compound flux, tapes etc shall be utilized.

The cable lugs shall be compressed on the conductor ends by means of tools. Insulating sleeves shall be furnished and covered over the bare ends of the connections so as to prevent accidental contact with the ground or with the adjacent terminals. The insulating sleeve shall be fire resistant and long enough to over pass the conductor insulation and shall be correct size of conductor used. The cables entering the control room from outdoor shall be sealed.

Standard cable grips and seals shall be utilized for cable pulling after pulling cable to cable markers shall be put to both ends of the cable and at the control room entry. The cable number and other data shall be punched and the cable markers are to be securely attached to the cables. Cable shall not be jointed and used for laying purpose. Sharp bending and kinking of cables shall be avoided. In each cable run, some extra length shall be kept at a suitable point. Control cable terminations shall be done in accordance with wiring diagram.

1.6	Lighting system: The equipment such as lighting distribution board, lighting panels, lighting fixtures lamps, wiring etc. are necessary for illuminating the switch yard. The lighting pillar box shall be erected . The box shall be grouted in cement concrete 1:4:8 with 40mm hard broken granite metal with foundation bolts.

1.7 	Support for fixtures: Mounting arrangement shall be 3M above ground level. Earthing shall be done with No.8GI wire. All lighting fixtures shall be assembled, installed and wired.

Reconductoring of Lines:

The existing conductor – copper, GI wire or aluminium conductor shall be replaced with the conductor specified in the document. The replaced conductor shall be wound and handed over to the section officer or nearest stores as per the instructions of the Engineer.

SECTION 6

SCHEDULE OF QUANTITIES AND PRICES

SECTION – 6

- PREAMBLE

- The Bill of Quantities shall be read in conjunction with the Instructions to Bidders.  General and Special Conditions of Contract, Technical Specifications and Drawings.

- The quantities given in the Bill of Quantities are estimated and provisional, and are given to provide a common basis for bidding.  The basis of payment will be the actual quantities of work ordered and carried out, as measured by the Contractor and verified by the Engineer and valued at the rates and prices tendered in the priced Bill of Quantities.  Where applicable and otherwise at such rates and  prices of the Engineer may fix within the terms of the Contract.

- The rates and prices tendered in the priced Bill of quantities shall, except in so far as it is otherwise provided under the Contract, include all constructional plant, labour, supervision materials, erection maintenance, insurance, profit.  Taxes and duties, together with all general risks, liabilities and obligations set out or implied in the contract.

- The whole cost of complying with provisions of the Contract shall be included in the items provided in the priced Bill of Quantities, and where no items are provided the cost shall be deemed to be distributed among the rates and prices entered for the related items of work.

- General directions and descriptions of work and materials are not necessarily repeated nor summarized in the Bill of Quantities.  References to the relevant sections of the contract documentation shall be made before entering prices against each item in the price Bill of Quantities

- The method of measurement of completed work which means supply erection and fixing of cross arms and other necessary auxilaries in case of PSCC polls and the payment shall be in accordance with relevant I.S.S. Codes.

7.        The method of measurement of completed work of payment shall be in

accordance with relavent I.S.S. Codes.

8.      	Rock defined as all materials which,  in the opinion of the Engineer require blasting or the use of metal wedges and sledge hammers or the use of compressed air drilling for  its removal and which cannot be extracted by ripping with tractor atleast with 150 BHP with single rear mounted heavy duty ripper.

| ANNEXURE -1A |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| LIST OF MATERIALS TO BE PROCURED BY THE CONTRACTOR |  |  |  |  |  |  |  |  |  |  |  |
| 1 | G.I. Bolts and nuts as per IS 6639 of 1972 and 12427 of 1988.(GKW make) |  |  |  |  |  |  |  |  |  |  |
| 2 | Spring Washers as per IS 3063 of 1972 |  |  |  |  |  |  |  |  |  |  |
| 3 | 16 mm, 18mm and 20mm MS rods as per IS 226 |  |  |  |  |  |  |  |  |  |  |
| 4 | Guard Wire 7/2.5 mm G.I. As per IS 2141 of 1968. |  |  |  |  |  |  |  |  |  |  |
| 5 | C.I. Earth Pipes |  |  |  |  |  |  |  |  |  |  |
| 6 | 38 mm H.B.G. metal / 20 mm HBG metal |  |  |  |  |  |  |  |  |  |  |
| 7 | Sand |  |  |  |  |  |  |  |  |  |  |
| 8 | Coke |  |  |  |  |  |  |  |  |  |  |
| 9 | Salt |  |  |  |  |  |  |  |  |  |  |
| 10 | Cement |  |  |  |  |  |  |  |  |  |  |
| 11 | Danger Board with Clamp |  |  |  |  |  |  |  |  |  |  |
| 12 | Earth Coils |  |  |  |  |  |  |  |  |  |  |
| 13 | Jointing Sleeves |  |  |  |  |  |  |  |  |  |  |
| 14 | Aluminium Binding wire 3.12 mm |  |  |  |  |  |  |  |  |  |  |
| 15 | Packing pieces. |  |  |  |  |  |  |  |  |  |  |
| 16 | White/Black Paint |  |  |  |  |  |  |  |  |  |  |
| 17 | G.I. Pipe 40 mm dia, & 2.5Mts. long |  |  |  |  |  |  |  |  |  |  |
| 18 | RCC Hume pipe, |  |  |  |  |  |  |  |  |  |  |
| 19 | 8 M/9.1m PSCC Poles |  |  |  |  |  |  |  |  |  |  |
| 20 | M.S. flat 50 x 6 mm / 75 x 8 mm for back lamps, for top cleat, stay clamps, bracing set. |  |  |  |  |  |  |  |  |  |  |
| 21 | R.S. Joists 152 x 152 mm |  |  |  |  |  |  |  |  |  |  |
| 22 | M.S. Channel 100 x 50 / 75 x 40 mm for 33 KV cross arm & 11 KV cross arms with M.S. Angle 65 x 65 x 6 mm |  |  |  |  |  |  |  |  |  |  |
| 23 | Stut poles |  |  |  |  |  |  |  |  |  |  |
| 24 | Any other matching materials required. |  |  |  |  |  |  |  |  |  |  |
| 25 | HT Insulators |  |  |  |  |  |  |  |  |  |  |
| 26 | Hardware fittings for item (25) |  |  |  |  |  |  |  |  |  |  |
| 27 | A.B. Switches (33KV 800 A, 11KV 400 & 200 A) |  |  |  |  |  |  |  |  |  |  |
| 28 | 100 Sq.mm AAA Conductor |  |  |  |  |  |  |  |  |  |  |
| 29 | 55 Sq.mm AAA Conductor |  |  |  |  |  |  |  |  |  |  |
| 30 | 200 Sq.mm ACSR panther conductor |  |  |  |  |  |  |  |  |  |  |
| 31 | MS Distribution Box with fuse units (for station transformer) and other wiring materials. |  |  |  |  |  |  |  |  |  |  |
|  | NOTE : | 1) The above material shall be procured by the contractor and transported to the site and cost shall be included in the relevant items of work in the schedule |  |  |  |  |  |  |  |  |  |
|  |  | 2) Any other materials connected with this work other than the items covered in this Annexure should also be supplied |  |  |  |  |  |  |  |  |  |

ANNEXURE – 2A

##### EQUIPMENT TO BE SUPPLIED BY APSPDCL FOR ERECTION OF             33/11 KV SUB-STATION

##### S.No.				Description

1)	Sub-Station Equipment :		Circuit Breakers with Control and Relay panels,

Power Transformers, instrument Transformers, Station Transformer.

Annexure-2 Contd….

ANNEXURE – 2B

##### MATERIALS TO BE SUPPLIED BY THE CONTRACTOR FOR ERECTION OF 33 KV/11 KV SUB-STATION

- Structure Accessories :

- Danger Boards

- Set of phase comprising Red, Yellow and Blue Plates

- Name Plate details

- Power Conductor Accessories :

- 33 KV and 11 KV Busbar clamps Suitable for 200 sq.  mm AAA Conductor.

- Tension clamps complete

- T Clamps, through clamps complete

- Pipe type earthing material : Cast Iron earth pipe 75 mm dia, 2750 mm long. 9.5 mm thick complete with G.I. bolt and nuts with washers.

- LT PVC/PVC Power Cable (Aluminium) / Control Cables (Copper)

- 2 x 4 sq. mm

- 2 x 25 sq.mm

- 2 core 2.5 sq mm copper cable

4 core 2.5 sq mm copper cable

10 core 2.5 sq mm copper cable

5)	33KV and 11KV HG Fuse sets.

6) 	a)	P.T. Marshalling Box (Pole mounted) of size 0.45 M X 0.45 M X 0.3 M fabricated    from sheet steel guage 16 with 8 way terminal block in battle gray paint.

- Yard lighting junction box (200 mm x 150 mm x 75 mm) fabricated from 3 thick sheet steel with fuse unit, and 8 way terminal block in battle gray paint.

- M.S. Plate 6 mm thick for base plate of support of structure.

- LT AC panel / LT distribution box of size 800 x 450 x 300 mm fabricated for 16 guage

sheet steel Nos. 63 Amps and 1 No. 100 Ams including wiring painting with battle gray

(DISTRIBUTION BOX Sketch enclosed).

- Supply of D.C. Annuciation panel.

- 125 W MV lamp fittings complete with mounting bracket arrangement.

- MS Rounds and Tor Steel as per ISS.

- MS Rounds 6mm

- MS Tor Steel 8 mm

- MS Tor Steel 10 mm

- MS Tor Steel 12 mm

- MS Gate Drawing enclosed.

- Fencing Posts: G.I. barbed wire and all other materials required for peripheral fencing.

- Fire fighting equipment and standard Tool box with Tools

- Binding wire MS bolts and nuts and all other matching materials required for successful commissioning of the Sub-Station.

- Cement.

- R.S. joists 152X152 mm. 8Mts. PSCC poles, M.S. channel 100x50 mm. M.S. flat            75X8mm and 50X6 mm, M.S. 65x65x6mm angle.

- Any other steel matching materials required.

19)        XLPE  U.G. Cables where ever required

20)        33 kV 800 A Isolators, 11 KV 400 A AB Switches, 11 KV 200 A AB Switches, 33 KV & 11KV LAs( both Station type & Line type) ,HT Insulators ,Post top Insulators,Hardware for HT Insulators and 33 kV HG fuse set complete.

NOTE: 1) The above materials shall be procured by the contractor and transported to the site & their cost shall be included in the relevant items of work in the schedules.

2) Any other material connected with the work other than covered in this Annexure should also be supplied.

21)	200 Sq.mm AAA Conductor for bus.

22)	24 volts, 40 AH trickle charger with sealed maintenance free lead acid batteries.

ANNEXURE – 3

###### TOOL BOX CONTAINING THE FOLLOWING T & P

- Tool Box size 20” x 10” X 15”

Standard Tool Box No.3 Tier Arrangement

- Tools (All the items from 2 (a) to 2 (d) should be of Taparia make).

a)	De Spanners 						15 Nos

(No.6 to 20)

b)	Ring Spanners 						15 Nos

(No.6 to 20)

- Screwdrivers

1.6” long						1 No.

2.9” long						1 No.

3.12” long						1 No.

4. Insulated screwdrivers 6” long			2 Nos.

d)	Tester 						2 Nos.

3.	11 KV  Insulated Hand Gloves				2 Nos.

4.	D.C. Voltmeter (5V-0-5V)				1 No.

5.	Pipe Wrench 12” long					1 No.

6.	Pipe Wrench 9” long					1 No.

7.	Hacksaw 12” long   			             	1 No.

8.	Torch Light (commander type)				1 No.

9.	Discharge rods with load wire (VIR 7/20 copper)		3 Nos.

15mts. Long including clamping arrangements

with copper strip to the rod (rod shall be of PVC)

complete.

SECTION 7

BILL OF QUANTITIES

|  |  |  |  | Rate |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Sl. No | Description of Item* | Quantity | Unit | In figures | In words | Amount |

- With brief specification and ref to Book of spn.

Note :

- Item for which no rate or price has been entered in will not be paid for by the Employer when executed and shall be deemed covered by the other rates and prices in the Bill of Quantities (refer: ITB Clause 13.2 and GCC Clause 43.3)

- Unit rates  and prices shall be quoted by the bidder in Indian rupee (ITB Clause 14.1).

- Where there is a discrepancy between the rate in figures and words, the rates in words will govern [ITB Clause 27. (a)].

- Where there is a discrepancy between the unit rate and the line item total resulting from multiplying the unit rate by quantity, the unit rate quoted shall govern [ITB Clause 27.1 (b)].

SECTION 8

FORMS OF SECURITIES

FORMS OF SECURITIES

Acceptable forms of securities are annexed.  Bidders should not complete the Performance Security forms at this time.  Only the successful Bidder will be required to provide Performance Security in accordance with one of the forms, or in a similar; for acceptable to the Employer.

Annex A:	Bid Security (Bank Guarantee)

Annex B:	Performance Bank Guarantee

ANNEXURE - A

BID SECURITY (BANK GUARANTEE)

Whereas ___________________________ (name of Bidder) (hereinafter called “the Bidder”) has submitted his biddated _________________________________ (date) for the construction of _________________________________ (name of Contract) hereinafter called “the Bid”).

KNOW ALL PEOPLE by these presents that We _____________________________ (name of Bank) of

___________________ (hereinafter called “the bank”) are bound unto ________________________ for

which payment well and truly to be made to the said Employer the Bank binds itself, his successors and assigns by these presents.

THE CONDITIONS of this obligation are :

- If after Bid opening the Bidder withdraws his bid during the period of Bid validity specified in the Form of Bid.

- If the Bidder having been notified of the acceptance of his bid by the Employer during the period of Bid Validity.

- Fails or refuses to execute the Form of Agreement in accordance with the instructions to Bidders, if required or

- Fails or refuses to furnish the Performance Security, in accordance with the instruction to Bidders ; or

- Does not accept the correction of the Bid Price pursuant Clause 27,

We undertake to pay to the Employer up to the above amount upon receipt of his first written demand, without the Employer having to substantiate his demand, provided that in his demand the Employer will note that the amount claimed by his is due to him owing ;to the occurrence of one or both of the two conditions, specifying the occurred condition or conditions.

This Guarantee will remain in force up to and including the date ______________________ 2 days after the deadline for submission of Bids as such deadline is stated in the Instructions to Bidders or as it may be extended by the Employer, notice of which extensions(s) to the Bank is hereby waived.  Any demand in respect of this guarantee should reach the Bank not later than the above date.

DATE __________________			Signature of the Bank

Witness ________________			Seal ________________________________

___________________________________________________________________________

(signature, name and address)

_________________________________

- The Bidder should insert the amount of the guarantee in words and figures denominated in Indian Rupees.  This figure should be the same as shown in Clause 16.1 of the Instructions to Bidders

- 45 days after the end of the validity period of the Bid.  Date should be inserted by the Employer before the Bidding documents are issued.

ANNEXURE - B

#### PERFORMANCE BANK GUARANTEE

To :	_________________________________________________ [name of Employer)

_________________________________________________ [address of Employer)

Whereas __________________________________________ [name and address of Contractor]

(hereinafter called “the Contractor”) has undertaken, in pursuance of Contract No. _______________dated ________________ to execute _______________ [name of Contract and brief

description of Works] (hereinafter called “the Contract”).

AND WHEREAS it has been stipulated by you in the said Contract that the Contractor shall furnish you with a Bank Guarantee by a recognized bank for the sum specified therein as security for compliance with his obligations in accordance with the Contract “

AND WHEREAS we have agreed to give the Contractor such a Bank Guarantee :

NOW THEREFORE we hereby affirm that we are the Guarantor and responsible to you, on behalf of the Contractor, up to a total of ___________________ [amount of guarantee] 1 ____________________ [in words], such sum being payable in the types and proportions of currencies in which the Contract Price is payable, and we undertake to pay you, upon your first written demand and ;without cavel or argument, any sum or ;sums within the limits of ___________________ [amount of guarantee]1 as aforesaid without your needing to prove or to show grounds or reasons for your demand for the sum specified therein.

We hereby waive the necessity of your demanding the said debt from the Contractor before presenting us with the demand.

We further agree that no change or addition to or other modification of the terms of the Contract or of the Works to be performed thereunder or of the Contract documents which may be made between you and the Contract hall in any way release us from any liability under this guarantee, and we hereby waive notice of any such change, addition or modification.

This guarantee shall be valid until 28 days from the date of expiry of the Defects Liability period

Signature and seal of the Guarantor ______________________

Name of Bank _______________________________________

Address _________________________

Date ____________________________

1.	An amount shall be inserted by the Guarantor, representing the percentage of the Contract Price specified in the Contract including additional security for unbalanced Bids, if any and denominated in Indian Rupees.

ANNEXURE - C

#### BANK GUARANTEE FOR ADVANCE PAYMENT

To :	_______________________________________________ [name of Employer]

_______________________________________________ [address of Employer]

_______________________________________________ [name of Contract]

Gentlemen :

In accordance with the provisions of the Conditions of Contract, sub-clause 51.1 (“Advance Payment”) of the above-mentioned Contract, _________________________ [name and address of  Contractor] (hereinafter called “the Contractor”) shall deposit with _________________________ [name of Employer] a bank guarantee to guarantee his proper and faithful performance under the said  Clause of the Contract in an amount of _______________ [amount of guarantee] 1 _________________________ [in words].

We, the ________________________________ [bank or financial institution], as instructed by the Contractor, agree unconditionally and irrecoverably to guarantee as primary obligator and not as Surety merely, the payment to ____________________ [name of Employed] on his first demand without whatsoever right of object on our part and ;without his first claim to the Contractor, in the amount not exceeding _____________________ [amount of ;guarantee]1 _____________________ [in words].

We further agree that no change or addition to or other modification of the terms of the Contract or of Works to be performed thereunder  or of any of the Contract documents which may be made between ______________ [name of Employer] and the Contractor, shall in any way release us from any liability under this guarantee, and we hereby waive notice of any such change, addition or modification.,

This guarantee shall remain valid and in full effect from the date of the advance payment under the Contract until _____________________ [name of Employer] receives full repayment of the same amount from the Contractor.

Yours truly,

Signature and seal : _____________________

Name of Bank/Financial Institution __________

Address : ______________________________

Date : ________________

1.	An amount shall be inserted by the bank or financial institution representing the amount of the Advance Payment, and denominated in Indian Rupees.

SECTION 9

DRAWINGS

LIST OF DRAWINGS FOR LINES & SUB-SATION

- CONDUCTOR FORMATION & CLEARANCES

- LINE DP STRUCTURE

- GUYING ARRANGEMENT SINGLE GUY

- GUYING ARRANGEMENT FLY GUY & BOW GUY

- GUY ASSEMBLY

- 33KV LINE TOP BRACKET

- 33KV LINE CONDUCTOR FORMATION AND CLEARANCES

- 11KV LINE SUPPORT WITH EARTH WIRE

- 11KV V CROSS ARM

- FIXING OF CROSS ARMS

- BACK CLAMP FOR CROSS ARMS

- TOP CLEAT FOR 33 KV & 11 KV LINES

- CROSSING OF LT POWER LINES (VERTICAL CONFIGURATION AND TELECOMMUNICATION LINES)

- 33KV LINES PROTECTIVE GUARDING ACROSS THE ROAD

- PIPE/ROD EARTHING

- COIL EARTHING

- RCC BASE / ANCHOR PLATE

- DOUBLE CIRCUIT ARRANGEMENT

- 9.1 M PSCC POLE

- 8.0 M PSCC POL.E

LIST OF DRAWINGS OF SUBSTATION

- STRUCTURAL LAYOUT 33/11KV S.S.

- SINGLE LINE DIAGRAM OF 33/11 KV S.S.

- EARTH MAT OF 33/11 KV S.S.

- MOUNTING OF 11KV HG FUSESET

- RETAINING WALL WITH SECURITY FENCING FOR SWITCH YARD

- POWER TRANSFORMER PLINTH

- CEMENT CONCRETE OF RS JOIST

- PLINTH FOR BREAKER

- LT AC PANEL

- C.I. PIPE EARTH ERECTION FOR SUBSTATION

- M.S. TUBULAR GATE

- PERIPHERAL FENCING

- PLAN OF CONTROL ROOM WITH OUT SECTION OFFICE

- PLAN OF CONTROL ROOM WITH SECTION OFFICE

- DISTRIBUTION TRANSFORMER IN SUB-STATION